## FOOTING
[5 empty] | PROJECT : | [9 empty] | PAGE :
[5 empty] | CLIENT : | [9 empty] | DESIGN BY :
[5 empty] | JOB NO. : |  |  |  | DATE : | [5 empty] | REVIEW BY :
Design of Footing at Piping Based on ACI 318-19
INPUT DATA & DESIGN SUMMARY
COLUMN WIDTH |  |  |  | c1 | = | 5 | in
COLUMN DEPTH |  |  |  | c2 | = | 5 | in
BASE PLATE WIDTH |  |  |  | b1 | = | 16 | in
BASE PLATE DEPTH |  |  |  | b2 | = | 16 | in
FOOTING CONCRETE STRENGTH |  |  |  | fc' | = | 2.5 | ksi
REBAR YIELD STRESS |  |  |  | fy | = | 60 | ksi
AXIAL DEAD LOAD |  |  |  | PDL | = | 40 | k
AXIAL LIVE LOAD |  |  |  | PLL | = | 25 | k
LATERAL LOAD (0=WIND, 1=SEISMIC) |  |  |  |  | = | 0 | Wind,SD | [9 empty] | <== Tips: | The ASCE 7-22 wind loads have been changed to SD level.
WIND AXIAL LOAD |  |  |  | PLAT | = | 20 | k, SD | [10 empty] | If ASCE 7-05, or early, the input wind loads should be increased by 1.6.
WIND MOMENT LOAD |  |  |  | MLAT | = | 96 | ft-k, SD
WIND SHEAR LOAD |  |  |  | VLAT | = | 2 | k, SD
SURCHARGE |  |  |  | qs | = | 0.1 | ksf
SOIL WEIGHT |  |  |  | ws | = | 0.11 | kcf
FOOTING EMBEDMENT DEPTH |  |  |  | Df | = | 3 | ft
FOOTING MIDDLE THICKNESS |  |  |  | T | = | 18 | in
SOIL COVER THICKNESS |  |  |  | D | = | 12 | in
ALLOW SOIL PRESSURE |  |  |  | Qa | = | 3 | ksf
SQUARE FOOTING LENGTH |  |  |  | L | = | 7 | ft
REINFORCING SIZE |  |  |  |  | # | 5
MIDDLE BOTTOM EACH WAY : |  |  |  |  | 9 # 5 @ 9 in o.c. |  |  |  |  | THE DESIGN IS INADEQUATE, SEE BELOW.
ANALYSIS
DESIGN LOADS (IBC SEC.1605.2 & ACI 318 5.3)
CASE 1: |  | DL + LL |  | P | = | 65 | kips
|  |  |  | M | = | 0 | ft-kips
CASE 2: |  | DL + LL + 0.6(1.3) W |  | P | = | 80.6 | kips
|  |  |  | M | = | 74.88 | ft-kips
CASE 3: |  | DL + LL + 0.6(0.65) W |  | P | = | 72.8 | kips
|  |  |  | M | = | 37.44 | ft-kips
CHECK OVERTURNING FACTOR (IBC 1605.2.1, 1808.3.1, & ASCE 7 12.13.4)
| MR / MO = |  | 6.4384 | > | F = 1.0 / 0.9 |  |  | [Satisfactory]
| Where | MO = | MLAT + VLAT Df - 0.5 PLAT L = |  |  |  | 32 | k-ft
|  | Pconc = | (0.15 kcf) L2 [T + 2 (Df - D - T) /3] = |  |  |  | 13.475 | k, footing wt
|  | Psoil = | ws D L2 = |  | 5.39 | k, soil weight
|  | MR = | 0.5 PDLL + 0.5 (Pconc + Psoil) L = |  |  |  | 206.0275 | k-ft
CHECK SOIL BEARING CAPACITY (ACI 318 13.3.1.1)
| Service Loads |  |  | CASE 1 |  |  | CASE 2 |  |  | CASE 3
| P |  |  | 65 |  |  | 80.6 |  |  | 72.8 |  |  | k
| qs L2 |  |  | 4.9 |  |  | 4.9 |  |  | 2.94 |  | k, (surcharge load)
| P conc - soil |  |  | 3.5933 |  |  | 3.5933 |  |  | 2.156 |  | k, (footing increased)
| S P |  |  | 73.4933 |  |  | 89.0933 |  |  | 77.896 |  |  | k
| S M |  |  | 0 |  |  | 74.88 |  |  | 37.44 |  |  | ft - k
| qmin |  |  | 2.2498 | > 0 |  | 1.3671 | > 0 |  | 1.7045 | > 0 |  | ksf, net pressure
| q3 |  |  | 2.2498 |  |  | 2.2739 |  |  | 2.1579 |  |  | ksf, net pressure
| q2 |  |  | 2.2498 |  |  | 3.1808 |  |  | 2.6113 |  |  | ksf, net pressure
| qmax |  |  | 2.2498 |  |  | 4.0876 |  |  | 3.0647 |  |  | ksf, net pressure
| qallow |  |  | 3 |  |  | 4 |  |  | 4 |  |  | ksf
(cont'd)
Where
[Unsatisfactory]
DESIGN FLEXURE & CHECK FLEXURE SHEAR (ACI 318 13.2.7, 21, & 22)
| Service Loads |  |  | CASE 1 |  |  | CASE 2 |  |  | CASE 3
| V |  |  | 36.7467 |  |  | 59.3581 |  |  | 46.3537 |  |  | k, flexure shear
| M |  |  | 69.6656 |  |  | 115.4131 |  |  | 89.3189 |  |  | ft - k, flexure moment
DESIGN FLEXURE
| Location |  |  | Mu,max = 1.5 M |  | d (in) | rmin | rreqD | rmax | smax |  | use |  | rprovD
| Middle Bottom Each Way |  |  | 173.1196 | ft-k | 14.6875 | 0.002206 | 0.0021878 | 0.012902 | 18 |  | 9 # 5 @ 9 in o.c. |  | 0.0022614
[Satisfactory]
CHECK FLEXURE SHEAR
| Direction |  |  | Vu,max = 1.5 V |  | fVc = 2 f b d (fc')0.5 |  |  |  | check Vu < f Vc
| Pipe Direction |  |  | 89.0371 | k |  | 92.5312 | k |  | [Satisfactory]
CHECK PUNCHING SHEAR (ACI 318 13.2.7.2, 22.6.4.1, 22.6.4.3, & 8.4.2.3)
| Case | Pu | Mu | b1 | b2 | b0 | gv | bc | y | Af | Ap | R | J | vu (psi) | f vc
| 1 | 97.5 | 0 | 25.1875 | 25.1875 | 100.75 | 0.4 | 1 | 2 | 32.6667 | 10.2762 | 0 | 8.1869 | 65.8888 | 150
| 2 | 120.9 | 112.32 | 25.1875 | 25.1875 | 100.75 | 0.4 | 1 | 2 | 32.6667 | 10.2762 | 0 | 8.1869 | 121.6974 | 150
| 3 | 109.2 | 56.16 | 25.1875 | 25.1875 | 100.75 | 0.4 | 1 | 2 | 32.6667 | 10.2762 | 0 | 8.1869 | 93.7931 | 150
[Satisfactory]
| where | f | = | 0.75 | (ACI 318 21.2)
|  | Pu | = | 1.5 Pcol
|  | Mu | = | 1.5 Mcol
LICENSE NUMBER: M 492263176 - XXXXXX XXXXXX, S.E. - ASCE 7-22 Package License
www.Engineering-International.com
|  |  | SIZE | DIAM. | AREA
|  |  | # | in | in2
|  |  | 3 | 0.375 | 0.11
|  |  | 4 | 0.5 | 0.2
|  |  | 5 | 0.625 | 0.31
|  |  | 6 | 0.75 | 0.44
|  |  | 7 | 0.875 | 0.6
|  |  | 8 | 1 | 0.79
|  |  | 9 | 1.128 | 1
|  |  | 10 | 1.27 | 1.27
|  |  | 11 | 1.41 | 1.56
|  |  | 14 | 1.693 | 2.25
|  |  | 18 | 2.257 | 4
|  | LONGITUDINAL REINF., BOT. |  |  |  | 9 | # | 5 | @ | 9 | in o.c.
140