## SHEAR WALL
|  |  |  | PROJECT : | [7 empty] | PAGE :
|  |  |  | CLIENT : | [7 empty] | DESIGN BY :
|  |  |  | JOB NO. : |  |  |  | DATE : |  |  |  | REVIEW BY :
Masonry Shear Wall Design Based on TMS 402-16/13 & 2021 IBC (both ASD and SD)
INPUT DATA & DESIGN SUMMARY
SPECIAL INSPECTION ( 0=NO, 1=YES ) |  |  |  |  | 1 | Yes
(This option only for local jurisdiction amendments to the code, not part of TMS.)
TYPE OF MASONRY ( 1=CMU, 2=BRICK ) |  |  |  |  | 1 | CMU
MASONRY STRENGTH |  |  |  | fm' = | 3 | ksi
REBAR YIELD STRESS |  |  |  | fy = | 60 | ksi
ALLOWABLE 30% INCREASING ? (Yes or No, IBC 1605.2) | [6 empty] | Yes
SEISMIC PERFORMANCE CATEGORY |  |  |  |  | D | Seismic D | [8 empty] | < == | D & E are for Special Reinforced Masonry Shear Wall, so R, W0, & Cd are 5, 2.5, & 3.5, otherwise 2, 2.5, & 1.75 (ASCE 7-33 Table 12.2-1).
( C,D,E, 0=WIND, 5=GRAVITY)
MASONRY LAID IN RUNNING BOND ? (TMS 402 7.3.2.6) | [7 empty] | Yes
SERVICE AXIAL LOAD |  |  |  | P = | 300 | kips, at middle of Lw
SERVICE SHEAR LOAD |  |  |  | Vx = | 190 | kips, (in-plane force)
SERVICE MOMENT LOAD |  |  | Mx = | 6200 | ft-kips, (top flange, bf1, compression)
|  |  | My = | 500 | ft-kips, (out-of-plane, left b11 & b21, compression)
EFFECTIVE HEIGHT OF WALL |  |  |  | hw = | 16 | ft
LENGTH OF SHEAR WALL |  |  |  | Lw = | 30 | ft, (within vertical control joints)
THE WALL DESIGN IS ADEQUATE.
THICKNESS OF WALL |  |  | tw = | 8 | in
REINFORCING OF WALL |  |  |  | 2 | # | 6 | at each ends, with |  | 8 | in center to edge.
|  | Ash, Horizontal | 1 | # | 6 | @ | 16 | in o.c.
|  | Asv, Vertical | 1 | # | 6 | @ | 24 | in o.c.
TOP FLANGE (COMPRESSION) |  |  |  | b11 = | 48 | in , | b12 = | 24 | in , | bf1 = | 80 | in ,(TMS 402 5.1.1.2.3)
| tf1 = | 12 | in , | 2 | # | 5 | @ | 48 | in o.c., Vertical
BOTTOM FLANGE |  |  |  | b21 = | 36 | in , | b22 = | 48 | in , | bf2 = | 92 | in ,(TMS 402 5.1.1.2.3)
| tf2 = | 8 | in , | 2 | # | 5 | @ | 48 | in o.c., Vertical
ANALYSIS
CHECK FLEXURAL & AXIAL CAPACITY BY ALLOWABLE STRESS DESIGN (ASD)
[15 empty] | < == | Tips: | Allowable P - M Interaction Diagram:
Point 1 is pure compression capacity based on Fb, which is much higher than allowable Pa.
Point 2 is the maximum moment capacity based on Fb.
Point 3 is the balanced point, when Fb & Fs con-currently.
Point 4 is the maximum pure moment based on Fb, which is not acceptable.
Point 5 is the maximum pure moment based on Fs.
P (k)
M (ft-k)
| P (load) = |  | 300 | kips | < | P (allowable) = Pa = |  |  | 2069.5566 | kips
| M (resultant) = (Mx2 + My2)0.5 = |  |  |  | 6220.1286 | ft-kips | < | M (allowable) = |  | 7571.5285 | ft-kips | [Satisfactory]
| Where | Em = | 2700 | ksi, (TMS 402 4.2.2.2.1) |  |  |  | An = | 4234.5 | in2
|  | Es = | 29000 | ksi, (TMS 402 4.2.2.1) |  |  |  | Ast = | 9.9433 | in2
|  | Scale Factor = |  | 1.3333 | , (TMS 402-11 2.1.2) |  |  | fs ≥ | 0 | ksi, (TMS 402 8.3.3.3)
|  | Fb = | 1.32 | ksi, (TMS 402 8-18) |  |  |  | h / r = | 87.2272 | , neglected conservatively flanges.
|  | Fs = | 32 | ksi, (TMS 402 8.3.3.1) |  |  |  | Pa = | 2069.5566 | kips, (TMS 402 8.3.4.2.1)
(cont'd)
CHECK FLEXURAL & AXIAL CAPACITY BY STRENGTH DESIGN (SD)
fPn (k)
| fMn (ft-k) | Solid Black Line - Tension Controlled
Solid Red Line - Transition
Dash Line - Compression Controlled
| Pu = 1.2 P = |  | 360 | kips |  |  | < | fPn = |  | 4729.0131 | kips, (TMS 402 9.3.4.1.1)
| Mu = (1/0.7) (Mx2 + My2)0.5 = |  |  |  | 8885.898 | ft-kips | < | fMn = |  | 12763.3047 | ft-kips, at Pu level.
[Satisfactory]
| Where | emu = | 0.0025 | , (TMS 402 9.3.2.c) |  |  | d = | 363.015 | in
|  | f = | 0.9 | , (TMS 402 9.1.4.1) |  |  | fm' = | 3 | ksi
CHECK SHEAR CAPACITY (ASD), (TMS 402 8.3.6)
Fv
| = | 105.7739 | psi | > | 1.5 | fv | = | 103.8251 | psi | [Satisfactory]
(factor 1.5 from TMS 402 7.3.2.6.1.2)
| Fv, Maximum | [8 empty] | 146.0593 | psi | > | 1.5 | fv
[Satisfactory]
CHECK MINIMUM REINFORCEMENTS
| Ash,min = | 0.06405 | in2/ft | < | Ash,actual = |  | 0.33 | in2/ft | [Satisfactory] |  | (TMS 402 7.3.2.6)
| Ssh,max = | 48 | in | > | Ssh,actual = |  | 16 | in | [Satisfactory] |  | (TMS 402 7.3.2.6)
| Asv,min = | 0.06405 | in2/ft | < | Asv,actual = |  | 0.22 | in2/ft | [Satisfactory] |  | (TMS 402 7.3.2.6)
| Ssv,max = | 48 | in | > | Ssv,actual = |  | 24 | in | [Satisfactory] |  | (TMS 402 7.3.2.6)
| Atotal,min = | 0.183 | in2/ft | < | Atotal,actual = |  | 0.55 | in2/ft | [Satisfactory] |  | (TMS 402 7.3.2.6)
CHECK MAXIMUM REINFORCEMENT PERCENTAGE
|  |  |  | 0.0087349 | > | r = | 0.00031792 | [Satisfactory]
(TMS 402 8.3.4.4)
LICENSE NUMBER: M 492263176 - XXXXXX XXXXXX, S.E. - ASCE 7-22 Package License
www.Engineering-International.com
#REF! | #REF!
#REF! | #REF!
#REF! | #REF!
.
130

## Pn-Mn (hidden)
| ecu = | 0.0025 | ,(Fig. R21.2.2a)
| Ec = | 3122.0186 | kips, (19.2.2.1b)
| Es = | 29000 | kips, (20.2.2.2)
| be = | 0.85 | ,(22.2.2.4.1)
| Fy = | 60 | ksi |  | Pu = | 360 | kips
| fc' = | 3 | ksi |  | Mu = | 8885.898 | ft-kips
| d = | 363.015 | in
| Ymax C to Top = | 183.5075 | in |  | fPMAX = | 4729.0131 | kips
| SAg = | 9.9433 | in2
| f = | 0.9 | ,(Fig. R21.2.2b)
|  | 0.9 | ,Tension Controlled
Compression Controlled | [10 empty] | c = | 198.6308 | in |  |  |  | c = | 159.2666 | in |  |  |  | c = | 119.9024 | in |  |  |  | c = | 198.6308 | in |  |  |  | c = | 222.9421 | in |  |  | c = | 247.2534 | in |  |  | c = | 271.5646 | in |  |  | c = | 295.8759 | in |  |  | c = | 320.1871 | in |  |  | c = | 344.4984 | in |  |  | c = | 368.8096 | in |  |  | c = | 393.1209 | in |  |  | c = | 417.4321 | in |  |  | c = | 441.7434 | in |  |  | c = | 466.0547 | in |  |  | c = | 490.3659 | in |  |  | c = | 514.6772 | in |  |  | c = | 538.9884 | in |  |  | c = | 563.2997 | in |  |  | c = | 587.6109 | in |  |  | c = | 611.9222 | in
[5 empty] | Local to C |  | Real to C |  |  | 0.0016336
|  | What | Element | Area | Xoc | Yoc | X | Y |  |  | e | fc | fs | F | M |  | e | fc | fs | F | M |  | e | fc | fs | F | M |  | e | fc | fs | F | M |  | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M
1 |  | Steel | 1 | 0.062 |  |  | -35.4526 | 177.424 |  |  | 0.0024234 |  | 60 | 3.72 | 660.0172 |  | 0.0024045 |  | 60 | 3.72 | 660.0172 |  | 0.0023732 |  | 60 | 3.72 | 660.0172 |  | 0.0024234 |  | 60 | 3.72 | 660.0172 |  | 0.0024318 |  | 60 | 3.72 | 660.0172 | 0.0024385 |  | 60 | 3.72 | 660.0172 | 0.002444 |  | 60 | 3.72 | 660.0172 | 0.0024486 |  | 60 | 3.72 | 660.0172 | 0.0024525 |  | 60 | 3.72 | 660.0172 | 0.0024559 |  | 60 | 3.72 | 660.0172 | 0.0024588 |  | 60 | 3.72 | 660.0172 | 0.0024613 |  | 60 | 3.72 | 660.0172 | 0.0024636 |  | 60 | 3.72 | 660.0172 | 0.0024656 |  | 60 | 3.72 | 660.0172 | 0.0024674 |  | 60 | 3.72 | 660.0172 | 0.002469 |  | 60 | 3.72 | 660.0172 | 0.0024704 |  | 60 | 3.72 | 660.0172 | 0.0024718 |  | 60 | 3.72 | 660.0172 | 0.002473 |  | 60 | 3.72 | 660.0172 | 0.0024741 |  | 60 | 3.72 | 660.0172 | 0.0024751 |  | 60 | 3.72 | 660.0172
2 |  | Steel | 2 | 0.062 |  |  | -30.6682 | 177.0381 |  |  | 0.0024186 |  | 60 | 3.72 | 658.5819 |  | 0.0023985 |  | 60 | 3.72 | 658.5819 |  | 0.0023651 |  | 60 | 3.72 | 658.5819 |  | 0.0024186 |  | 60 | 3.72 | 658.5819 |  | 0.0024275 |  | 60 | 3.72 | 658.5819 | 0.0024346 |  | 60 | 3.72 | 658.5819 | 0.0024404 |  | 60 | 3.72 | 658.5819 | 0.0024453 |  | 60 | 3.72 | 658.5819 | 0.0024495 |  | 60 | 3.72 | 658.5819 | 0.0024531 |  | 60 | 3.72 | 658.5819 | 0.0024561 |  | 60 | 3.72 | 658.5819 | 0.0024589 |  | 60 | 3.72 | 658.5819 | 0.0024613 |  | 60 | 3.72 | 658.5819 | 0.0024634 |  | 60 | 3.72 | 658.5819 | 0.0024653 |  | 60 | 3.72 | 658.5819 | 0.002467 |  | 60 | 3.72 | 658.5819 | 0.0024686 |  | 60 | 3.72 | 658.5819 | 0.00247 |  | 60 | 3.72 | 658.5819 | 0.0024713 |  | 60 | 3.72 | 658.5819 | 0.0024725 |  | 60 | 3.72 | 658.5819 | 0.0024736 |  | 60 | 3.72 | 658.5819
3 |  | Steel | 3 | 0.062 |  |  | -25.8837 | 176.6523 |  |  | 0.0024137 |  | 60 | 3.72 | 657.1465 |  | 0.0023924 |  | 60 | 3.72 | 657.1465 |  | 0.0023571 |  | 60 | 3.72 | 657.1465 |  | 0.0024137 |  | 60 | 3.72 | 657.1465 |  | 0.0024231 |  | 60 | 3.72 | 657.1465 | 0.0024307 |  | 60 | 3.72 | 657.1465 | 0.0024369 |  | 60 | 3.72 | 657.1465 | 0.0024421 |  | 60 | 3.72 | 657.1465 | 0.0024465 |  | 60 | 3.72 | 657.1465 | 0.0024503 |  | 60 | 3.72 | 657.1465 | 0.0024535 |  | 60 | 3.72 | 657.1465 | 0.0024564 |  | 60 | 3.72 | 657.1465 | 0.0024589 |  | 60 | 3.72 | 657.1465 | 0.0024612 |  | 60 | 3.72 | 657.1465 | 0.0024632 |  | 60 | 3.72 | 657.1465 | 0.0024651 |  | 60 | 3.72 | 657.1465 | 0.0024667 |  | 60 | 3.72 | 657.1465 | 0.0024682 |  | 60 | 3.72 | 657.1465 | 0.0024696 |  | 60 | 3.72 | 657.1465 | 0.0024708 |  | 60 | 3.72 | 657.1465 | 0.002472 |  | 60 | 3.72 | 657.1465
4 |  | Steel | 4 | 0.062 |  |  | -21.0992 | 176.2665 |  |  | 0.0024089 |  | 60 | 3.72 | 655.7112 |  | 0.0023863 |  | 60 | 3.72 | 655.7112 |  | 0.002349 |  | 60 | 3.72 | 655.7112 |  | 0.0024089 |  | 60 | 3.72 | 655.7112 |  | 0.0024188 |  | 60 | 3.72 | 655.7112 | 0.0024268 |  | 60 | 3.72 | 655.7112 | 0.0024333 |  | 60 | 3.72 | 655.7112 | 0.0024388 |  | 60 | 3.72 | 655.7112 | 0.0024435 |  | 60 | 3.72 | 655.7112 | 0.0024475 |  | 60 | 3.72 | 655.7112 | 0.0024509 |  | 60 | 3.72 | 655.7112 | 0.002454 |  | 60 | 3.72 | 655.7112 | 0.0024566 |  | 60 | 3.72 | 655.7112 | 0.002459 |  | 60 | 3.72 | 655.7112 | 0.0024612 |  | 60 | 3.72 | 655.7112 | 0.0024631 |  | 60 | 3.72 | 655.7112 | 0.0024648 |  | 60 | 3.72 | 655.7112 | 0.0024664 |  | 60 | 3.72 | 655.7112 | 0.0024679 |  | 60 | 3.72 | 655.7112 | 0.0024692 |  | 60 | 3.72 | 655.7112 | 0.0024704 |  | 60 | 3.72 | 655.7112
5 |  | Steel | 5 | 0.062 |  |  | -16.3148 | 175.8806 |  |  | 0.002404 |  | 60 | 3.72 | 654.2759 |  | 0.0023803 |  | 60 | 3.72 | 654.2759 |  | 0.002341 |  | 60 | 3.72 | 654.2759 |  | 0.002404 |  | 60 | 3.72 | 654.2759 |  | 0.0024145 |  | 60 | 3.72 | 654.2759 | 0.0024229 |  | 60 | 3.72 | 654.2759 | 0.0024298 |  | 60 | 3.72 | 654.2759 | 0.0024356 |  | 60 | 3.72 | 654.2759 | 0.0024404 |  | 60 | 3.72 | 654.2759 | 0.0024447 |  | 60 | 3.72 | 654.2759 | 0.0024483 |  | 60 | 3.72 | 654.2759 | 0.0024515 |  | 60 | 3.72 | 654.2759 | 0.0024543 |  | 60 | 3.72 | 654.2759 | 0.0024568 |  | 60 | 3.72 | 654.2759 | 0.0024591 |  | 60 | 3.72 | 654.2759 | 0.0024611 |  | 60 | 3.72 | 654.2759 | 0.002463 |  | 60 | 3.72 | 654.2759 | 0.0024646 |  | 60 | 3.72 | 654.2759 | 0.0024662 |  | 60 | 3.72 | 654.2759 | 0.0024676 |  | 60 | 3.72 | 654.2759 | 0.0024688 |  | 60 | 3.72 | 654.2759
6 |  | Steel | 6 | 0.062 |  |  | -11.5303 | 175.4948 |  |  | 0.0023992 |  | 60 | 3.72 | 652.8405 |  | 0.0023742 |  | 60 | 3.72 | 652.8405 |  | 0.0023329 |  | 60 | 3.72 | 652.8405 |  | 0.0023992 |  | 60 | 3.72 | 652.8405 |  | 0.0024101 |  | 60 | 3.72 | 652.8405 | 0.002419 |  | 60 | 3.72 | 652.8405 | 0.0024262 |  | 60 | 3.72 | 652.8405 | 0.0024323 |  | 60 | 3.72 | 652.8405 | 0.0024374 |  | 60 | 3.72 | 652.8405 | 0.0024419 |  | 60 | 3.72 | 652.8405 | 0.0024457 |  | 60 | 3.72 | 652.8405 | 0.002449 |  | 60 | 3.72 | 652.8405 | 0.002452 |  | 60 | 3.72 | 652.8405 | 0.0024547 |  | 60 | 3.72 | 652.8405 | 0.002457 |  | 60 | 3.72 | 652.8405 | 0.0024591 |  | 60 | 3.72 | 652.8405 | 0.0024611 |  | 60 | 3.72 | 652.8405 | 0.0024628 |  | 60 | 3.72 | 652.8405 | 0.0024644 |  | 60 | 3.72 | 652.8405 | 0.0024659 |  | 60 | 3.72 | 652.8405 | 0.0024673 |  | 60 | 3.72 | 652.8405
7 |  | Steel | 7 | 0.062 |  |  | -6.7458 | 175.1089 |  |  | 0.0023943 |  | 60 | 3.72 | 651.4052 |  | 0.0023682 |  | 60 | 3.72 | 651.4052 |  | 0.0023249 |  | 60 | 3.72 | 651.4052 |  | 0.0023943 |  | 60 | 3.72 | 651.4052 |  | 0.0024058 |  | 60 | 3.72 | 651.4052 | 0.0024151 |  | 60 | 3.72 | 651.4052 | 0.0024227 |  | 60 | 3.72 | 651.4052 | 0.002429 |  | 60 | 3.72 | 651.4052 | 0.0024344 |  | 60 | 3.72 | 651.4052 | 0.0024391 |  | 60 | 3.72 | 651.4052 | 0.0024431 |  | 60 | 3.72 | 651.4052 | 0.0024466 |  | 60 | 3.72 | 651.4052 | 0.0024497 |  | 60 | 3.72 | 651.4052 | 0.0024525 |  | 60 | 3.72 | 651.4052 | 0.0024549 |  | 60 | 3.72 | 651.4052 | 0.0024572 |  | 60 | 3.72 | 651.4052 | 0.0024592 |  | 60 | 3.72 | 651.4052 | 0.002461 |  | 60 | 3.72 | 651.4052 | 0.0024627 |  | 60 | 3.72 | 651.4052 | 0.0024643 |  | 60 | 3.72 | 651.4052 | 0.0024657 |  | 60 | 3.72 | 651.4052
8 |  | Steel | 8 | 0.062 |  |  | -1.9614 | 174.7231 |  |  | 0.0023894 |  | 60 | 3.72 | 649.9698 |  | 0.0023621 |  | 60 | 3.72 | 649.9698 |  | 0.0023168 |  | 60 | 3.72 | 649.9698 |  | 0.0023894 |  | 60 | 3.72 | 649.9698 |  | 0.0024015 |  | 60 | 3.72 | 649.9698 | 0.0024112 |  | 60 | 3.72 | 649.9698 | 0.0024191 |  | 60 | 3.72 | 649.9698 | 0.0024258 |  | 60 | 3.72 | 649.9698 | 0.0024314 |  | 60 | 3.72 | 649.9698 | 0.0024363 |  | 60 | 3.72 | 649.9698 | 0.0024405 |  | 60 | 3.72 | 649.9698 | 0.0024441 |  | 60 | 3.72 | 649.9698 | 0.0024474 |  | 60 | 3.72 | 649.9698 | 0.0024503 |  | 60 | 3.72 | 649.9698 | 0.0024529 |  | 60 | 3.72 | 649.9698 | 0.0024552 |  | 60 | 3.72 | 649.9698 | 0.0024573 |  | 60 | 3.72 | 649.9698 | 0.0024593 |  | 60 | 3.72 | 649.9698 | 0.002461 |  | 60 | 3.72 | 649.9698 | 0.0024626 |  | 60 | 3.72 | 649.9698 | 0.0024641 |  | 60 | 3.72 | 649.9698
9 |  | Steel | 9 | 0.062 |  |  | 2.8231 | 174.3372 |  |  | 0.0023846 |  | 60 | 3.72 | 648.5345 |  | 0.0023561 |  | 60 | 3.72 | 648.5345 |  | 0.0023088 |  | 60 | 3.72 | 648.5345 |  | 0.0023846 |  | 60 | 3.72 | 648.5345 |  | 0.0023972 |  | 60 | 3.72 | 648.5345 | 0.0024073 |  | 60 | 3.72 | 648.5345 | 0.0024156 |  | 60 | 3.72 | 648.5345 | 0.0024225 |  | 60 | 3.72 | 648.5345 | 0.0024284 |  | 60 | 3.72 | 648.5345 | 0.0024335 |  | 60 | 3.72 | 648.5345 | 0.0024378 |  | 60 | 3.72 | 648.5345 | 0.0024417 |  | 60 | 3.72 | 648.5345 | 0.0024451 |  | 60 | 3.72 | 648.5345 | 0.0024481 |  | 60 | 3.72 | 648.5345 | 0.0024508 |  | 60 | 3.72 | 648.5345 | 0.0024532 |  | 60 | 3.72 | 648.5345 | 0.0024555 |  | 60 | 3.72 | 648.5345 | 0.0024575 |  | 60 | 3.72 | 648.5345 | 0.0024593 |  | 60 | 3.72 | 648.5345 | 0.002461 |  | 60 | 3.72 | 648.5345 | 0.0024625 |  | 60 | 3.72 | 648.5345
10 |  | Steel | 10 | 0.062 |  |  | 7.6076 | 173.9514 |  |  | 0.0023797 |  | 60 | 3.72 | 647.0992 |  | 0.00235 |  | 60 | 3.72 | 647.0992 |  | 0.0023008 |  | 60 | 3.72 | 647.0992 |  | 0.0023797 |  | 60 | 3.72 | 647.0992 |  | 0.0023928 |  | 60 | 3.72 | 647.0992 | 0.0024034 |  | 60 | 3.72 | 647.0992 | 0.002412 |  | 60 | 3.72 | 647.0992 | 0.0024193 |  | 60 | 3.72 | 647.0992 | 0.0024254 |  | 60 | 3.72 | 647.0992 | 0.0024307 |  | 60 | 3.72 | 647.0992 | 0.0024352 |  | 60 | 3.72 | 647.0992 | 0.0024392 |  | 60 | 3.72 | 647.0992 | 0.0024428 |  | 60 | 3.72 | 647.0992 | 0.0024459 |  | 60 | 3.72 | 647.0992 | 0.0024487 |  | 60 | 3.72 | 647.0992 | 0.0024513 |  | 60 | 3.72 | 647.0992 | 0.0024536 |  | 60 | 3.72 | 647.0992 | 0.0024557 |  | 60 | 3.72 | 647.0992 | 0.0024576 |  | 60 | 3.72 | 647.0992 | 0.0024593 |  | 60 | 3.72 | 647.0992 | 0.002461 |  | 60 | 3.72 | 647.0992
11 |  | Steel | 11 | 0.062 |  |  | 40.7001 | 171.2826 |  |  | 0.0023461 |  | 60 | 3.72 | 637.1714 |  | 0.0023081 |  | 60 | 3.72 | 637.1714 |  | 0.0022451 |  | 60 | 3.72 | 637.1714 |  | 0.0023461 |  | 60 | 3.72 | 637.1714 |  | 0.0023629 |  | 60 | 3.72 | 637.1714 | 0.0023764 |  | 60 | 3.72 | 637.1714 | 0.0023875 |  | 60 | 3.72 | 637.1714 | 0.0023967 |  | 60 | 3.72 | 637.1714 | 0.0024045 |  | 60 | 3.72 | 637.1714 | 0.0024113 |  | 60 | 3.72 | 637.1714 | 0.0024171 |  | 60 | 3.72 | 637.1714 | 0.0024223 |  | 60 | 3.72 | 637.1714 | 0.0024268 |  | 60 | 3.72 | 637.1714 | 0.0024308 |  | 60 | 3.72 | 637.1714 | 0.0024344 |  | 60 | 3.72 | 637.1714 | 0.0024377 |  | 60 | 3.72 | 637.1714 | 0.0024406 |  | 60 | 3.72 | 637.1714 | 0.0024433 |  | 60 | 3.72 | 637.1714 | 0.0024457 |  | 60 | 3.72 | 637.1714 | 0.002448 |  | 60 | 3.72 | 637.1714 | 0.0024501 |  | 60 | 3.72 | 637.1714
12 |  | Steel | 12 | 0.062 |  |  | 38.3079 | 171.4756 |  |  | 0.0023486 |  | 60 | 3.72 | 637.8891 |  | 0.0023111 |  | 60 | 3.72 | 637.8891 |  | 0.0022491 |  | 60 | 3.72 | 637.8891 |  | 0.0023486 |  | 60 | 3.72 | 637.8891 |  | 0.0023651 |  | 60 | 3.72 | 637.8891 | 0.0023783 |  | 60 | 3.72 | 637.8891 | 0.0023892 |  | 60 | 3.72 | 637.8891 | 0.0023983 |  | 60 | 3.72 | 637.8891 | 0.0024061 |  | 60 | 3.72 | 637.8891 | 0.0024127 |  | 60 | 3.72 | 637.8891 | 0.0024184 |  | 60 | 3.72 | 637.8891 | 0.0024235 |  | 60 | 3.72 | 637.8891 | 0.0024279 |  | 60 | 3.72 | 637.8891 | 0.0024319 |  | 60 | 3.72 | 637.8891 | 0.0024355 |  | 60 | 3.72 | 637.8891 | 0.0024387 |  | 60 | 3.72 | 637.8891 | 0.0024416 |  | 60 | 3.72 | 637.8891 | 0.0024442 |  | 60 | 3.72 | 637.8891 | 0.0024466 |  | 60 | 3.72 | 637.8891 | 0.0024488 |  | 60 | 3.72 | 637.8891 | 0.0024508 |  | 60 | 3.72 | 637.8891
13 |  | Steel | 13 | 0.062 |  |  | 35.9157 | 171.6685 |  |  | 0.002351 |  | 60 | 3.72 | 638.6067 |  | 0.0023142 |  | 60 | 3.72 | 638.6067 |  | 0.0022532 |  | 60 | 3.72 | 638.6067 |  | 0.002351 |  | 60 | 3.72 | 638.6067 |  | 0.0023672 |  | 60 | 3.72 | 638.6067 | 0.0023803 |  | 60 | 3.72 | 638.6067 | 0.002391 |  | 60 | 3.72 | 638.6067 | 0.0024 |  | 60 | 3.72 | 638.6067 | 0.0024076 |  | 60 | 3.72 | 638.6067 | 0.0024141 |  | 60 | 3.72 | 638.6067 | 0.0024197 |  | 60 | 3.72 | 638.6067 | 0.0024247 |  | 60 | 3.72 | 638.6067 | 0.0024291 |  | 60 | 3.72 | 638.6067 | 0.002433 |  | 60 | 3.72 | 638.6067 | 0.0024365 |  | 60 | 3.72 | 638.6067 | 0.0024396 |  | 60 | 3.72 | 638.6067 | 0.0024425 |  | 60 | 3.72 | 638.6067 | 0.0024451 |  | 60 | 3.72 | 638.6067 | 0.0024475 |  | 60 | 3.72 | 638.6067 | 0.0024496 |  | 60 | 3.72 | 638.6067 | 0.0024516 |  | 60 | 3.72 | 638.6067
14 |  | Steel | 14 | 0.062 |  |  | 33.5234 | 171.8614 |  |  | 0.0023534 |  | 60 | 3.72 | 639.3244 |  | 0.0023172 |  | 60 | 3.72 | 639.3244 |  | 0.0022572 |  | 60 | 3.72 | 639.3244 |  | 0.0023534 |  | 60 | 3.72 | 639.3244 |  | 0.0023694 |  | 60 | 3.72 | 639.3244 | 0.0023822 |  | 60 | 3.72 | 639.3244 | 0.0023928 |  | 60 | 3.72 | 639.3244 | 0.0024016 |  | 60 | 3.72 | 639.3244 | 0.0024091 |  | 60 | 3.72 | 639.3244 | 0.0024155 |  | 60 | 3.72 | 639.3244 | 0.0024211 |  | 60 | 3.72 | 639.3244 | 0.0024259 |  | 60 | 3.72 | 639.3244 | 0.0024303 |  | 60 | 3.72 | 639.3244 | 0.0024341 |  | 60 | 3.72 | 639.3244 | 0.0024375 |  | 60 | 3.72 | 639.3244 | 0.0024406 |  | 60 | 3.72 | 639.3244 | 0.0024434 |  | 60 | 3.72 | 639.3244 | 0.002446 |  | 60 | 3.72 | 639.3244 | 0.0024483 |  | 60 | 3.72 | 639.3244 | 0.0024505 |  | 60 | 3.72 | 639.3244 | 0.0024524 |  | 60 | 3.72 | 639.3244
15 |  | Steel | 15 | 0.062 |  |  | 31.1312 | 172.0543 |  |  | 0.0023558 |  | 60 | 3.72 | 640.0421 |  | 0.0023202 |  | 60 | 3.72 | 640.0421 |  | 0.0022612 |  | 60 | 3.72 | 640.0421 |  | 0.0023558 |  | 60 | 3.72 | 640.0421 |  | 0.0023716 |  | 60 | 3.72 | 640.0421 | 0.0023842 |  | 60 | 3.72 | 640.0421 | 0.0023946 |  | 60 | 3.72 | 640.0421 | 0.0024032 |  | 60 | 3.72 | 640.0421 | 0.0024106 |  | 60 | 3.72 | 640.0421 | 0.0024169 |  | 60 | 3.72 | 640.0421 | 0.0024224 |  | 60 | 3.72 | 640.0421 | 0.0024272 |  | 60 | 3.72 | 640.0421 | 0.0024314 |  | 60 | 3.72 | 640.0421 | 0.0024352 |  | 60 | 3.72 | 640.0421 | 0.0024386 |  | 60 | 3.72 | 640.0421 | 0.0024416 |  | 60 | 3.72 | 640.0421 | 0.0024444 |  | 60 | 3.72 | 640.0421 | 0.0024469 |  | 60 | 3.72 | 640.0421 | 0.0024492 |  | 60 | 3.72 | 640.0421 | 0.0024513 |  | 60 | 3.72 | 640.0421 | 0.0024532 |  | 60 | 3.72 | 640.0421
16 |  | Steel | 16 | 0.062 |  |  | 28.739 | 172.2472 |  |  | 0.0023583 |  | 60 | 3.72 | 640.7597 |  | 0.0023232 |  | 60 | 3.72 | 640.7597 |  | 0.0022652 |  | 60 | 3.72 | 640.7597 |  | 0.0023583 |  | 60 | 3.72 | 640.7597 |  | 0.0023737 |  | 60 | 3.72 | 640.7597 | 0.0023861 |  | 60 | 3.72 | 640.7597 | 0.0023963 |  | 60 | 3.72 | 640.7597 | 0.0024049 |  | 60 | 3.72 | 640.7597 | 0.0024121 |  | 60 | 3.72 | 640.7597 | 0.0024183 |  | 60 | 3.72 | 640.7597 | 0.0024237 |  | 60 | 3.72 | 640.7597 | 0.0024284 |  | 60 | 3.72 | 640.7597 | 0.0024326 |  | 60 | 3.72 | 640.7597 | 0.0024363 |  | 60 | 3.72 | 640.7597 | 0.0024396 |  | 60 | 3.72 | 640.7597 | 0.0024426 |  | 60 | 3.72 | 640.7597 | 0.0024453 |  | 60 | 3.72 | 640.7597 | 0.0024478 |  | 60 | 3.72 | 640.7597 | 0.00245 |  | 60 | 3.72 | 640.7597 | 0.0024521 |  | 60 | 3.72 | 640.7597 | 0.002454 |  | 60 | 3.72 | 640.7597
17 |  | Steel | 17 | 0.062 |  |  | 26.3467 | 172.4402 |  |  | 0.0023607 |  | 60 | 3.72 | 641.4774 |  | 0.0023263 |  | 60 | 3.72 | 641.4774 |  | 0.0022692 |  | 60 | 3.72 | 641.4774 |  | 0.0023607 |  | 60 | 3.72 | 641.4774 |  | 0.0023759 |  | 60 | 3.72 | 641.4774 | 0.0023881 |  | 60 | 3.72 | 641.4774 | 0.0023981 |  | 60 | 3.72 | 641.4774 | 0.0024065 |  | 60 | 3.72 | 641.4774 | 0.0024136 |  | 60 | 3.72 | 641.4774 | 0.0024197 |  | 60 | 3.72 | 641.4774 | 0.002425 |  | 60 | 3.72 | 641.4774 | 0.0024296 |  | 60 | 3.72 | 641.4774 | 0.0024337 |  | 60 | 3.72 | 641.4774 | 0.0024374 |  | 60 | 3.72 | 641.4774 | 0.0024406 |  | 60 | 3.72 | 641.4774 | 0.0024436 |  | 60 | 3.72 | 641.4774 | 0.0024462 |  | 60 | 3.72 | 641.4774 | 0.0024487 |  | 60 | 3.72 | 641.4774 | 0.0024509 |  | 60 | 3.72 | 641.4774 | 0.0024529 |  | 60 | 3.72 | 641.4774 | 0.0024548 |  | 60 | 3.72 | 641.4774
18 |  | Steel | 18 | 0.062 |  |  | 23.9545 | 172.6331 |  |  | 0.0023631 |  | 60 | 3.72 | 642.1951 |  | 0.0023293 |  | 60 | 3.72 | 642.1951 |  | 0.0022733 |  | 60 | 3.72 | 642.1951 |  | 0.0023631 |  | 60 | 3.72 | 642.1951 |  | 0.0023781 |  | 60 | 3.72 | 642.1951 | 0.00239 |  | 60 | 3.72 | 642.1951 | 0.0023999 |  | 60 | 3.72 | 642.1951 | 0.0024081 |  | 60 | 3.72 | 642.1951 | 0.0024151 |  | 60 | 3.72 | 642.1951 | 0.0024211 |  | 60 | 3.72 | 642.1951 | 0.0024263 |  | 60 | 3.72 | 642.1951 | 0.0024308 |  | 60 | 3.72 | 642.1951 | 0.0024349 |  | 60 | 3.72 | 642.1951 | 0.0024385 |  | 60 | 3.72 | 642.1951 | 0.0024417 |  | 60 | 3.72 | 642.1951 | 0.0024446 |  | 60 | 3.72 | 642.1951 | 0.0024472 |  | 60 | 3.72 | 642.1951 | 0.0024496 |  | 60 | 3.72 | 642.1951 | 0.0024517 |  | 60 | 3.72 | 642.1951 | 0.0024537 |  | 60 | 3.72 | 642.1951 | 0.0024556 |  | 60 | 3.72 | 642.1951
19 |  | Steel | 19 | 0.062 |  |  | 21.5623 | 172.826 |  |  | 0.0023656 |  | 60 | 3.72 | 642.9128 |  | 0.0023323 |  | 60 | 3.72 | 642.9128 |  | 0.0022773 |  | 60 | 3.72 | 642.9128 |  | 0.0023656 |  | 60 | 3.72 | 642.9128 |  | 0.0023802 |  | 60 | 3.72 | 642.9128 | 0.002392 |  | 60 | 3.72 | 642.9128 | 0.0024017 |  | 60 | 3.72 | 642.9128 | 0.0024097 |  | 60 | 3.72 | 642.9128 | 0.0024166 |  | 60 | 3.72 | 642.9128 | 0.0024225 |  | 60 | 3.72 | 642.9128 | 0.0024276 |  | 60 | 3.72 | 642.9128 | 0.0024321 |  | 60 | 3.72 | 642.9128 | 0.002436 |  | 60 | 3.72 | 642.9128 | 0.0024395 |  | 60 | 3.72 | 642.9128 | 0.0024427 |  | 60 | 3.72 | 642.9128 | 0.0024455 |  | 60 | 3.72 | 642.9128 | 0.0024481 |  | 60 | 3.72 | 642.9128 | 0.0024505 |  | 60 | 3.72 | 642.9128 | 0.0024526 |  | 60 | 3.72 | 642.9128 | 0.0024546 |  | 60 | 3.72 | 642.9128 | 0.0024564 |  | 60 | 3.72 | 642.9128
20 |  | Steel | 20 | 0.062 |  |  | 19.17 | 173.0189 |  |  | 0.002368 |  | 60 | 3.72 | 643.6304 |  | 0.0023354 |  | 60 | 3.72 | 643.6304 |  | 0.0022813 |  | 60 | 3.72 | 643.6304 |  | 0.002368 |  | 60 | 3.72 | 643.6304 |  | 0.0023824 |  | 60 | 3.72 | 643.6304 | 0.0023939 |  | 60 | 3.72 | 643.6304 | 0.0024034 |  | 60 | 3.72 | 643.6304 | 0.0024114 |  | 60 | 3.72 | 643.6304 | 0.0024181 |  | 60 | 3.72 | 643.6304 | 0.0024239 |  | 60 | 3.72 | 643.6304 | 0.0024289 |  | 60 | 3.72 | 643.6304 | 0.0024333 |  | 60 | 3.72 | 643.6304 | 0.0024372 |  | 60 | 3.72 | 643.6304 | 0.0024406 |  | 60 | 3.72 | 643.6304 | 0.0024437 |  | 60 | 3.72 | 643.6304 | 0.0024465 |  | 60 | 3.72 | 643.6304 | 0.0024491 |  | 60 | 3.72 | 643.6304 | 0.0024514 |  | 60 | 3.72 | 643.6304 | 0.0024535 |  | 60 | 3.72 | 643.6304 | 0.0024554 |  | 60 | 3.72 | 643.6304 | 0.0024571 |  | 60 | 3.72 | 643.6304
21 |  | Steel | 21 | 0.22 |  |  | 14.3084 | 177.424 |  |  | 0.0024234 |  | 60 | 13.2 | 2341.9966 |  | 0.0024045 |  | 60 | 13.2 | 2341.9966 |  | 0.0023732 |  | 60 | 13.2 | 2341.9966 |  | 0.0024234 |  | 60 | 13.2 | 2341.9966 |  | 0.0024318 |  | 60 | 13.2 | 2341.9966 | 0.0024385 |  | 60 | 13.2 | 2341.9966 | 0.002444 |  | 60 | 13.2 | 2341.9966 | 0.0024486 |  | 60 | 13.2 | 2341.9966 | 0.0024525 |  | 60 | 13.2 | 2341.9966 | 0.0024559 |  | 60 | 13.2 | 2341.9966 | 0.0024588 |  | 60 | 13.2 | 2341.9966 | 0.0024613 |  | 60 | 13.2 | 2341.9966 | 0.0024636 |  | 60 | 13.2 | 2341.9966 | 0.0024656 |  | 60 | 13.2 | 2341.9966 | 0.0024674 |  | 60 | 13.2 | 2341.9966 | 0.002469 |  | 60 | 13.2 | 2341.9966 | 0.0024704 |  | 60 | 13.2 | 2341.9966 | 0.0024718 |  | 60 | 13.2 | 2341.9966 | 0.002473 |  | 60 | 13.2 | 2341.9966 | 0.0024741 |  | 60 | 13.2 | 2341.9966 | 0.0024751 |  | 60 | 13.2 | 2341.9966
22 |  | Steel | 22 | 0.22 |  |  | 13.9868 | 173.4369 |  |  | 0.0023733 |  | 60 | 13.2 | 2289.3675 |  | 0.0023419 |  | 60 | 13.2 | 2289.3675 |  | 0.00229 |  | 60 | 13.2 | 2289.3675 |  | 0.0023733 |  | 60 | 13.2 | 2289.3675 |  | 0.0023871 |  | 60 | 13.2 | 2289.3675 | 0.0023982 |  | 60 | 13.2 | 2289.3675 | 0.0024073 |  | 60 | 13.2 | 2289.3675 | 0.0024149 |  | 60 | 13.2 | 2289.3675 | 0.0024214 |  | 60 | 13.2 | 2289.3675 | 0.0024269 |  | 60 | 13.2 | 2289.3675 | 0.0024317 |  | 60 | 13.2 | 2289.3675 | 0.002436 |  | 60 | 13.2 | 2289.3675 | 0.0024397 |  | 60 | 13.2 | 2289.3675 | 0.002443 |  | 60 | 13.2 | 2289.3675 | 0.002446 |  | 60 | 13.2 | 2289.3675 | 0.0024487 |  | 60 | 13.2 | 2289.3675 | 0.0024511 |  | 60 | 13.2 | 2289.3675 | 0.0024533 |  | 60 | 13.2 | 2289.3675 | 0.0024553 |  | 60 | 13.2 | 2289.3675 | 0.0024572 |  | 60 | 13.2 | 2289.3675 | 0.0024589 |  | 60 | 13.2 | 2289.3675
23 |  | Steel | 23 | 0.22 |  |  | 13.6653 | 169.4499 |  |  | 0.0023231 |  | 60 | 13.2 | 2236.7383 |  | 0.0022793 |  | 60 | 13.2 | 2236.7383 |  | 0.0022069 |  | 60 | 13.2 | 2236.7383 |  | 0.0023231 |  | 60 | 13.2 | 2236.7383 |  | 0.0023424 |  | 60 | 13.2 | 2236.7383 | 0.0023579 |  | 60 | 13.2 | 2236.7383 | 0.0023706 |  | 60 | 13.2 | 2236.7383 | 0.0023812 |  | 60 | 13.2 | 2236.7383 | 0.0023902 |  | 60 | 13.2 | 2236.7383 | 0.002398 |  | 60 | 13.2 | 2236.7383 | 0.0024047 |  | 60 | 13.2 | 2236.7383 | 0.0024106 |  | 60 | 13.2 | 2236.7383 | 0.0024158 |  | 60 | 13.2 | 2236.7383 | 0.0024204 |  | 60 | 13.2 | 2236.7383 | 0.0024246 |  | 60 | 13.2 | 2236.7383 | 0.0024283 |  | 60 | 13.2 | 2236.7383 | 0.0024317 |  | 60 | 13.2 | 2236.7383 | 0.0024348 |  | 60 | 13.2 | 2236.7383 | 0.0024376 |  | 60 | 13.2 | 2236.7383 | 0.0024402 |  | 60 | 13.2 | 2236.7383 | 0.0024426 |  | 60 | 13.2 | 2236.7383
24 |  | Steel | 24 | 0.22 |  |  | 13.3438 | 165.4628 |  |  | 0.0022729 |  | 60 | 13.2 | 2184.1092 |  | 0.0022168 |  | 60 | 13.2 | 2184.1092 |  | 0.0021238 |  | 60 | 13.2 | 2184.1092 |  | 0.0022729 |  | 60 | 13.2 | 2184.1092 |  | 0.0022977 |  | 60 | 13.2 | 2184.1092 | 0.0023175 |  | 60 | 13.2 | 2184.1092 | 0.0023339 |  | 60 | 13.2 | 2184.1092 | 0.0023475 |  | 60 | 13.2 | 2184.1092 | 0.0023591 |  | 60 | 13.2 | 2184.1092 | 0.0023691 |  | 60 | 13.2 | 2184.1092 | 0.0023777 |  | 60 | 13.2 | 2184.1092 | 0.0023852 |  | 60 | 13.2 | 2184.1092 | 0.0023919 |  | 60 | 13.2 | 2184.1092 | 0.0023979 |  | 60 | 13.2 | 2184.1092 | 0.0024032 |  | 60 | 13.2 | 2184.1092 | 0.002408 |  | 60 | 13.2 | 2184.1092 | 0.0024123 |  | 60 | 13.2 | 2184.1092 | 0.0024163 |  | 60 | 13.2 | 2184.1092 | 0.0024199 |  | 60 | 13.2 | 2184.1092 | 0.0024232 |  | 60 | 13.2 | 2184.1092 | 0.0024263 |  | 60 | 13.2 | 2184.1092
25 |  | Steel | 25 | 0.15033 |  |  | 12.8534 | 159.3826 |  |  | 0.0021964 |  | 60 | 9.02 | 1437.6307 |  | 0.0021213 |  | 60 | 9.02 | 1437.6307 |  | 0.001997 |  | 57.9127 | 8.7062 | 1387.6168 |  | 0.0021964 |  | 60 | 9.02 | 1437.6307 |  | 0.0022295 |  | 60 | 9.02 | 1437.6307 | 0.0022561 |  | 60 | 9.02 | 1437.6307 | 0.0022779 |  | 60 | 9.02 | 1437.6307 | 0.0022962 |  | 60 | 9.02 | 1437.6307 | 0.0023116 |  | 60 | 9.02 | 1437.6307 | 0.0023249 |  | 60 | 9.02 | 1437.6307 | 0.0023365 |  | 60 | 9.02 | 1437.6307 | 0.0023466 |  | 60 | 9.02 | 1437.6307 | 0.0023555 |  | 60 | 9.02 | 1437.6307 | 0.0023635 |  | 60 | 9.02 | 1437.6307 | 0.0023706 |  | 60 | 9.02 | 1437.6307 | 0.002377 |  | 60 | 9.02 | 1437.6307 | 0.0023828 |  | 60 | 9.02 | 1437.6307 | 0.0023881 |  | 60 | 9.02 | 1437.6307 | 0.0023929 |  | 60 | 9.02 | 1437.6307 | 0.0023974 |  | 60 | 9.02 | 1437.6307 | 0.0024014 |  | 60 | 9.02 | 1437.6307
26 |  | Steel | 26 | 0.15033 |  |  | 12.1943 | 151.2091 |  |  | 0.0020935 |  | 60 | 9.02 | 1363.906 |  | 0.001993 |  | 57.7974 | 8.6889 | 1313.8369 |  | 0.0018266 |  | 52.9705 | 7.9632 | 1204.1131 |  | 0.0020935 |  | 60 | 9.02 | 1363.906 |  | 0.0021378 |  | 60 | 9.02 | 1363.906 | 0.0021734 |  | 60 | 9.02 | 1363.906 | 0.0022027 |  | 60 | 9.02 | 1363.906 | 0.0022271 |  | 60 | 9.02 | 1363.906 | 0.0022478 |  | 60 | 9.02 | 1363.906 | 0.0022656 |  | 60 | 9.02 | 1363.906 | 0.0022811 |  | 60 | 9.02 | 1363.906 | 0.0022946 |  | 60 | 9.02 | 1363.906 | 0.0023066 |  | 60 | 9.02 | 1363.906 | 0.0023172 |  | 60 | 9.02 | 1363.906 | 0.0023267 |  | 60 | 9.02 | 1363.906 | 0.0023353 |  | 60 | 9.02 | 1363.906 | 0.0023431 |  | 60 | 9.02 | 1363.906 | 0.0023502 |  | 60 | 9.02 | 1363.906 | 0.0023567 |  | 60 | 9.02 | 1363.906 | 0.0023626 |  | 60 | 9.02 | 1363.906 | 0.002368 |  | 60 | 9.02 | 1363.906
27 |  | Steel | 27 | 0.15033 |  |  | 11.5351 | 143.0356 |  |  | 0.0019906 |  | 57.7278 | 8.6784 | 1241.3226 |  | 0.0018647 |  | 54.0767 | 8.1295 | 1162.8134 |  | 0.0016561 |  | 48.0283 | 7.2203 | 1032.7547 |  | 0.0019906 |  | 57.7278 | 8.6784 | 1241.3226 |  | 0.0020462 |  | 59.3387 | 8.9206 | 1275.9611 | 0.0020908 |  | 60 | 9.02 | 1290.1814 | 0.0021274 |  | 60 | 9.02 | 1290.1814 | 0.002158 |  | 60 | 9.02 | 1290.1814 | 0.002184 |  | 60 | 9.02 | 1290.1814 | 0.0022063 |  | 60 | 9.02 | 1290.1814 | 0.0022257 |  | 60 | 9.02 | 1290.1814 | 0.0022426 |  | 60 | 9.02 | 1290.1814 | 0.0022576 |  | 60 | 9.02 | 1290.1814 | 0.002271 |  | 60 | 9.02 | 1290.1814 | 0.0022829 |  | 60 | 9.02 | 1290.1814 | 0.0022937 |  | 60 | 9.02 | 1290.1814 | 0.0023034 |  | 60 | 9.02 | 1290.1814 | 0.0023123 |  | 60 | 9.02 | 1290.1814 | 0.0023204 |  | 60 | 9.02 | 1290.1814 | 0.0023278 |  | 60 | 9.02 | 1290.1814 | 0.0023347 |  | 60 | 9.02 | 1290.1814
28 |  | Steel | 28 | 0.15033 |  |  | 10.876 | 134.8622 |  |  | 0.0018877 |  | 54.7445 | 8.2299 | 1109.9056 |  | 0.0017364 |  | 50.3561 | 7.5702 | 1020.9333 |  | 0.0014857 |  | 43.0862 | 6.4773 | 873.5416 |  | 0.0018877 |  | 54.7445 | 8.2299 | 1109.9056 |  | 0.0019545 |  | 56.6807 | 8.521 | 1149.1604 | 0.0020081 |  | 58.2361 | 8.7548 | 1180.6957 | 0.0020522 |  | 59.5131 | 8.9468 | 1206.5848 | 0.002089 |  | 60 | 9.02 | 1216.4567 | 0.0021202 |  | 60 | 9.02 | 1216.4567 | 0.002147 |  | 60 | 9.02 | 1216.4567 | 0.0021703 |  | 60 | 9.02 | 1216.4567 | 0.0021906 |  | 60 | 9.02 | 1216.4567 | 0.0022087 |  | 60 | 9.02 | 1216.4567 | 0.0022247 |  | 60 | 9.02 | 1216.4567 | 0.0022391 |  | 60 | 9.02 | 1216.4567 | 0.002252 |  | 60 | 9.02 | 1216.4567 | 0.0022637 |  | 60 | 9.02 | 1216.4567 | 0.0022744 |  | 60 | 9.02 | 1216.4567 | 0.0022841 |  | 60 | 9.02 | 1216.4567 | 0.002293 |  | 60 | 9.02 | 1216.4567 | 0.0023013 |  | 60 | 9.02 | 1216.4567
29 |  | Steel | 29 | 0.15033 |  |  | 10.2168 | 126.6887 |  |  | 0.0017849 |  | 51.7612 | 7.7814 | 985.8199 |  | 0.0016081 |  | 46.6354 | 7.0109 | 888.1967 |  | 0.0013153 |  | 38.144 | 5.7343 | 726.4737 |  | 0.0017849 |  | 51.7612 | 7.7814 | 985.8199 |  | 0.0018629 |  | 54.0227 | 8.1214 | 1028.8916 | 0.0019255 |  | 55.8395 | 8.3945 | 1063.4932 | 0.0019769 |  | 57.331 | 8.6188 | 1091.8996 | 0.0020199 |  | 58.5774 | 8.8061 | 1115.6378 | 0.0020564 |  | 59.6345 | 8.9651 | 1135.7712 | 0.0020877 |  | 60 | 9.02 | 1142.7321 | 0.0021149 |  | 60 | 9.02 | 1142.7321 | 0.0021387 |  | 60 | 9.02 | 1142.7321 | 0.0021597 |  | 60 | 9.02 | 1142.7321 | 0.0021784 |  | 60 | 9.02 | 1142.7321 | 0.0021952 |  | 60 | 9.02 | 1142.7321 | 0.0022103 |  | 60 | 9.02 | 1142.7321 | 0.002224 |  | 60 | 9.02 | 1142.7321 | 0.0022365 |  | 60 | 9.02 | 1142.7321 | 0.0022478 |  | 60 | 9.02 | 1142.7321 | 0.0022583 |  | 60 | 9.02 | 1142.7321 | 0.0022679 |  | 60 | 9.02 | 1142.7321
30 |  | Steel | 30 | 0.15033 |  |  | 9.5577 | 118.5152 |  |  | 0.001682 |  | 48.7779 | 7.3329 | 869.0658 |  | 0.0014798 |  | 42.9148 | 6.4515 | 764.6036 |  | 0.0011449 |  | 33.2019 | 4.9914 | 591.5512 |  | 0.001682 |  | 48.7779 | 7.3329 | 869.0658 |  | 0.0017712 |  | 51.3647 | 7.7218 | 915.1548 | 0.0018429 |  | 53.4429 | 8.0342 | 952.1804 | 0.0019017 |  | 55.1489 | 8.2907 | 982.5767 | 0.0019508 |  | 56.5746 | 8.505 | 1007.9779 | 0.0019925 |  | 57.7838 | 8.6868 | 1029.5218 | 0.0020284 |  | 58.8223 | 8.843 | 1048.0249 | 0.0020594 |  | 59.7239 | 8.9785 | 1064.0887 | 0.0020867 |  | 60 | 9.02 | 1069.0074 | 0.0021108 |  | 60 | 9.02 | 1069.0074 | 0.0021322 |  | 60 | 9.02 | 1069.0074 | 0.0021514 |  | 60 | 9.02 | 1069.0074 | 0.0021687 |  | 60 | 9.02 | 1069.0074 | 0.0021843 |  | 60 | 9.02 | 1069.0074 | 0.0021985 |  | 60 | 9.02 | 1069.0074 | 0.0022116 |  | 60 | 9.02 | 1069.0074 | 0.0022235 |  | 60 | 9.02 | 1069.0074 | 0.0022345 |  | 60 | 9.02 | 1069.0074
31 |  | Steel | 31 | 0.15033 |  |  | 8.8985 | 110.3418 |  |  | 0.0015791 |  | 45.7946 | 6.8845 | 759.643 |  | 0.0013515 |  | 39.1941 | 5.8922 | 650.1539 |  | 0.00097447 |  | 28.2597 | 4.2484 | 468.7739 |  | 0.0015791 |  | 45.7946 | 6.8845 | 759.643 |  | 0.0016795 |  | 48.7068 | 7.3222 | 807.9499 | 0.0017602 |  | 51.0462 | 7.674 | 846.7573 | 0.0018264 |  | 52.9668 | 7.9627 | 878.6164 | 0.0018818 |  | 54.5718 | 8.204 | 905.2399 | 0.0019287 |  | 55.9331 | 8.4086 | 927.8205 | 0.001969 |  | 57.1022 | 8.5844 | 947.214 | 0.002004 |  | 58.1172 | 8.737 | 964.0508 | 0.0020347 |  | 59.0067 | 8.8707 | 978.8051 | 0.0020618 |  | 59.7925 | 8.9888 | 991.8409 | 0.0020859 |  | 60 | 9.02 | 995.2828 | 0.0021075 |  | 60 | 9.02 | 995.2828 | 0.002127 |  | 60 | 9.02 | 995.2828 | 0.0021446 |  | 60 | 9.02 | 995.2828 | 0.0021606 |  | 60 | 9.02 | 995.2828 | 0.0021753 |  | 60 | 9.02 | 995.2828 | 0.0021887 |  | 60 | 9.02 | 995.2828 | 0.0022011 |  | 60 | 9.02 | 995.2828
32 |  | Steel | 32 | 0.15033 |  |  | 8.2394 | 102.1683 |  |  | 0.0014763 |  | 42.8113 | 6.436 | 657.5517 |  | 0.0012232 |  | 35.4735 | 5.3328 | 544.8477 |  | 0.00080405 |  | 23.3176 | 3.5054 | 358.1419 |  | 0.0014763 |  | 42.8113 | 6.436 | 657.5517 |  | 0.0015879 |  | 46.0488 | 6.9227 | 707.277 | 0.0016776 |  | 48.6496 | 7.3137 | 747.2239 | 0.0017512 |  | 50.7848 | 7.6346 | 780.0184 | 0.0018127 |  | 52.569 | 7.9029 | 807.4237 | 0.0018649 |  | 54.0824 | 8.1304 | 830.6673 | 0.0019097 |  | 55.3821 | 8.3258 | 850.6303 | 0.0019486 |  | 56.5105 | 8.4954 | 867.9614 | 0.0019827 |  | 57.4993 | 8.6441 | 883.149 | 0.0020129 |  | 58.3729 | 8.7754 | 896.5675 | 0.0020397 |  | 59.1504 | 8.8923 | 908.5091 | 0.0020637 |  | 59.8468 | 8.997 | 919.2048 | 0.0020853 |  | 60 | 9.02 | 921.5581 | 0.0021049 |  | 60 | 9.02 | 921.5581 | 0.0021227 |  | 60 | 9.02 | 921.5581 | 0.002139 |  | 60 | 9.02 | 921.5581 | 0.0021539 |  | 60 | 9.02 | 921.5581 | 0.0021677 |  | 60 | 9.02 | 921.5581
33 |  | Steel | 33 | 0.15033 |  |  | 7.5802 | 93.9948 |  |  | 0.0013734 |  | 39.828 | 5.9875 | 562.7918 |  | 0.0010949 |  | 31.7528 | 4.7735 | 448.685 |  | 0.00063364 |  | 18.3754 | 2.7624 | 259.6552 |  | 0.0013734 |  | 39.828 | 5.9875 | 562.7918 |  | 0.0014962 |  | 43.3908 | 6.5231 | 613.1361 | 0.0015949 |  | 46.253 | 6.9534 | 653.5802 | 0.001676 |  | 48.6027 | 7.3066 | 686.7829 | 0.0017437 |  | 50.5662 | 7.6018 | 714.5293 | 0.0018011 |  | 52.2316 | 7.8522 | 738.0622 | 0.0018504 |  | 53.662 | 8.0672 | 758.2737 | 0.0018932 |  | 54.9037 | 8.2539 | 775.8206 | 0.0019308 |  | 55.9919 | 8.4175 | 791.1972 | 0.0019639 |  | 56.9534 | 8.562 | 804.7827 | 0.0019934 |  | 57.809 | 8.6906 | 816.8729 | 0.0020198 |  | 58.5753 | 8.8058 | 827.7018 | 0.0020436 |  | 59.2657 | 8.9096 | 837.4569 | 0.0020652 |  | 59.8908 | 9.0036 | 846.2904 | 0.0020848 |  | 60 | 9.02 | 847.8335 | 0.0021027 |  | 60 | 9.02 | 847.8335 | 0.0021192 |  | 60 | 9.02 | 847.8335 | 0.0021343 |  | 60 | 9.02 | 847.8335
34 |  | Steel | 34 | 0.15033 |  |  | 6.9211 | 85.8214 |  |  | 0.0012705 |  | 36.8447 | 5.539 | 475.3634 |  | 0.00096663 |  | 28.0322 | 4.2142 | 361.6657 |  | 0.00046322 |  | 13.4333 | 2.0195 | 173.3137 |  | 0.0012705 |  | 36.8447 | 5.539 | 475.3634 |  | 0.0014046 |  | 40.7328 | 6.1235 | 525.5271 | 0.0015123 |  | 43.8563 | 6.5931 | 565.8262 | 0.0016007 |  | 46.4206 | 6.9786 | 598.9098 | 0.0016746 |  | 48.5635 | 7.3007 | 626.5567 | 0.0017373 |  | 50.3809 | 7.5739 | 650.0053 | 0.0017911 |  | 51.9419 | 7.8086 | 670.1443 | 0.0018378 |  | 53.297 | 8.0123 | 687.6282 | 0.0018788 |  | 54.4846 | 8.1908 | 702.9497 | 0.001915 |  | 55.5338 | 8.3486 | 716.4865 | 0.0019472 |  | 56.4675 | 8.4889 | 728.5334 | 0.001976 |  | 57.3038 | 8.6147 | 739.3234 | 0.002002 |  | 58.0572 | 8.7279 | 749.0435 | 0.0020255 |  | 58.7394 | 8.8305 | 757.8454 | 0.0020469 |  | 59.3601 | 8.9238 | 765.8532 | 0.0020665 |  | 59.9272 | 9.0091 | 773.1698 | 0.0020844 |  | 60 | 9.02 | 774.1088 | 0.0021009 |  | 60 | 9.02 | 774.1088
35 |  | Steel | 35 | 0.15033 |  |  | 6.2619 | 77.6479 |  |  | 0.0011676 |  | 33.8614 | 5.0905 | 395.2663 |  | 0.00083833 |  | 24.3115 | 3.6548 | 283.7899 |  | 0.0002928 |  | 8.4911 | 1.2765 | 99.1176 |  | 0.0011676 |  | 33.8614 | 5.0905 | 395.2663 |  | 0.0013129 |  | 38.0748 | 5.7239 | 444.4501 | 0.0014296 |  | 41.4597 | 6.2328 | 483.9619 | 0.0015255 |  | 44.2385 | 6.6505 | 516.3992 | 0.0016055 |  | 46.5607 | 6.9996 | 543.506 | 0.0016735 |  | 48.5302 | 7.2957 | 566.4964 | 0.0017318 |  | 50.2218 | 7.55 | 586.242 | 0.0017824 |  | 51.6903 | 7.7708 | 603.3844 | 0.0018268 |  | 52.9772 | 7.9642 | 618.4065 | 0.001866 |  | 54.1142 | 8.1352 | 631.6789 | 0.0019009 |  | 55.1261 | 8.2873 | 643.4904 | 0.0019322 |  | 56.0324 | 8.4235 | 654.0696 | 0.0019603 |  | 56.8488 | 8.5463 | 663.5999 | 0.0019858 |  | 57.5881 | 8.6574 | 672.2298 | 0.002009 |  | 58.2607 | 8.7585 | 680.0811 | 0.0020302 |  | 58.8752 | 8.8509 | 687.2548 | 0.0020496 |  | 59.4389 | 8.9357 | 693.8349 | 0.0020675 |  | 59.9578 | 9.0137 | 699.8921
36 |  | Steel | 36 | 0.15033 |  |  | 5.6028 | 69.4744 |  |  | 0.0010648 |  | 30.8781 | 4.642 | 322.5008 |  | 0.00071003 |  | 20.5909 | 3.0955 | 215.0575 |  | 0.00012238 |  | 3.549 | 0.53353 | 37.0667 |  | 0.0010648 |  | 30.8781 | 4.642 | 322.5008 |  | 0.0012213 |  | 35.4168 | 5.3243 | 369.9051 | 0.001347 |  | 39.0631 | 5.8725 | 407.9873 | 0.0014502 |  | 42.0564 | 6.3225 | 439.251 | 0.0015365 |  | 44.5579 | 6.6985 | 465.3771 | 0.0016096 |  | 46.6795 | 7.0175 | 487.5357 | 0.0016725 |  | 48.5016 | 7.2914 | 506.5669 | 0.001727 |  | 50.0836 | 7.5292 | 523.0891 | 0.0017748 |  | 51.4698 | 7.7376 | 537.5677 | 0.0018171 |  | 52.6946 | 7.9218 | 550.3599 | 0.0018546 |  | 53.7846 | 8.0856 | 561.7441 | 0.0018883 |  | 54.7609 | 8.2324 | 571.9405 | 0.0019186 |  | 55.6404 | 8.3646 | 581.1259 | 0.0019461 |  | 56.4367 | 8.4843 | 589.4436 | 0.0019711 |  | 57.1613 | 8.5932 | 597.0109 | 0.0019939 |  | 57.8233 | 8.6928 | 603.9251 | 0.0020148 |  | 58.4305 | 8.7841 | 610.2671 | 0.0020341 |  | 58.9895 | 8.8681 | 616.1052
37 |  | Steel | 37 | 0.15033 |  |  | 4.9436 | 61.301 |  |  | 0.00096189 |  | 27.8948 | 4.1935 | 257.0666 |  | 0.00058173 |  | 16.8702 | 2.5362 | 155.4687 |  | -4.804e-05 |  | -1.3932 | -0.20944 | -12.8389 |  | 0.00096189 |  | 27.8948 | 4.1935 | 257.0666 |  | 0.0011296 |  | 32.7589 | 4.9247 | 301.892 | 0.0012644 |  | 36.6664 | 5.5122 | 337.9024 | 0.001375 |  | 39.8743 | 5.9944 | 367.4653 | 0.0014674 |  | 42.5551 | 6.3975 | 392.17 | 0.0015458 |  | 44.8288 | 6.7393 | 413.1231 | 0.0016132 |  | 46.7815 | 7.0328 | 431.119 | 0.0016716 |  | 48.4768 | 7.2877 | 446.7423 | 0.0017228 |  | 49.9625 | 7.511 | 460.4332 | 0.0017681 |  | 51.2751 | 7.7084 | 472.5295 | 0.0018084 |  | 52.4432 | 7.884 | 483.2943 | 0.0018445 |  | 53.4894 | 8.0412 | 492.936 | 0.001877 |  | 54.4319 | 8.1829 | 501.6217 | 0.0019064 |  | 55.2854 | 8.3112 | 509.4869 | 0.0019332 |  | 56.0619 | 8.428 | 516.6425 | 0.0019576 |  | 56.7713 | 8.5346 | 523.1805 | 0.0019801 |  | 57.422 | 8.6324 | 529.1775 | 0.0020007 |  | 58.0211 | 8.7225 | 534.698
38 |  | Steel | 38 | 0.15033 |  |  | 4.2845 | 53.1275 |  |  | 0.00085902 |  | 24.9115 | 3.745 | 198.9639 |  | 0.00045343 |  | 13.1495 | 1.9768 | 105.0232 |  | -0.00021846 |  | -6.3353 | -0.95241 | -50.5992 |  | 0.00085902 |  | 24.9115 | 3.745 | 198.9639 |  | 0.001038 |  | 30.1009 | 4.5252 | 240.4108 | 0.0011817 |  | 34.2698 | 5.1519 | 273.7072 | 0.0012997 |  | 37.6923 | 5.6664 | 301.042 | 0.0013984 |  | 40.5523 | 6.0964 | 323.8847 | 0.001482 |  | 42.978 | 6.461 | 343.2587 | 0.0015538 |  | 45.0614 | 6.7742 | 359.8982 | 0.0016162 |  | 46.8701 | 7.0461 | 374.344 | 0.0016709 |  | 48.4551 | 7.2844 | 387.0031 | 0.0017192 |  | 49.8555 | 7.4949 | 398.1876 | 0.0017621 |  | 51.1017 | 7.6823 | 408.1411 | 0.0018006 |  | 52.2179 | 7.8501 | 417.0562 | 0.0018353 |  | 53.2235 | 8.0013 | 425.0873 | 0.0018667 |  | 54.134 | 8.1381 | 432.3596 | 0.0018953 |  | 54.9624 | 8.2627 | 438.9759 | 0.0019214 |  | 55.7193 | 8.3765 | 445.0212 | 0.0019453 |  | 56.4136 | 8.4808 | 450.5662 | 0.0019673 |  | 57.0527 | 8.5769 | 455.6706
39 |  | Steel | 39 | 0.15033 |  |  | 3.6253 | 44.9541 |  |  | 0.00075614 |  | 21.9282 | 3.2965 | 148.1926 |  | 0.00032513 |  | 9.4289 | 1.4175 | 63.7213 |  | -0.00038888 |  | -11.2775 | -1.6954 | -76.2142 |  | 0.00075614 |  | 21.9282 | 3.2965 | 148.1926 |  | 0.00094631 |  | 27.4429 | 4.1256 | 185.4617 | 0.0010991 |  | 31.8732 | 4.7916 | 215.4017 | 0.0012245 |  | 35.5102 | 5.3384 | 239.9811 | 0.0013293 |  | 38.5495 | 5.7953 | 260.5213 | 0.0014182 |  | 41.1273 | 6.1828 | 277.9423 | 0.0014945 |  | 43.3413 | 6.5156 | 292.9045 | 0.0015608 |  | 45.2634 | 6.8046 | 305.8942 | 0.0016189 |  | 46.9477 | 7.0578 | 317.2772 | 0.0016702 |  | 48.4359 | 7.2815 | 327.3344 | 0.0017159 |  | 49.7603 | 7.4806 | 336.2845 | 0.0017568 |  | 50.9465 | 7.659 | 344.3009 | 0.0017936 |  | 52.015 | 7.8196 | 351.5225 | 0.001827 |  | 52.9827 | 7.9651 | 358.0618 | 0.0018573 |  | 53.863 | 8.0974 | 364.0112 | 0.0018851 |  | 54.6674 | 8.2183 | 369.447 | 0.0019105 |  | 55.4051 | 8.3292 | 374.4331 | 0.0019339 |  | 56.0843 | 8.4313 | 379.023
40 |  | Steel | 40 | 0.15033 |  |  | 2.9662 | 36.7806 |  |  | 0.00065327 |  | 18.9449 | 2.848 | 104.7528 |  | 0.00019684 |  | 5.7082 | 0.85814 | 31.5628 |  | -0.0005593 |  | -16.2196 | -2.4384 | -89.684 |  | 0.00065327 |  | 18.9449 | 2.848 | 104.7528 |  | 0.00085465 |  | 24.7849 | 3.726 | 137.0444 | 0.0010164 |  | 29.4765 | 4.4313 | 162.9859 | 0.0011492 |  | 33.3281 | 5.0103 | 184.2827 | 0.0012602 |  | 36.5467 | 5.4942 | 202.0797 | 0.0013544 |  | 39.2766 | 5.9046 | 217.1741 | 0.0014352 |  | 41.6212 | 6.2571 | 230.1381 | 0.0015054 |  | 43.6567 | 6.5631 | 241.3929 | 0.0015669 |  | 45.4404 | 6.8312 | 251.2557 | 0.0016213 |  | 47.0163 | 7.0681 | 259.9697 | 0.0016696 |  | 48.4188 | 7.279 | 267.7246 | 0.0017129 |  | 49.675 | 7.4678 | 274.6704 | 0.001752 |  | 50.8066 | 7.6379 | 280.9274 | 0.0017873 |  | 51.8313 | 7.792 | 286.5934 | 0.0018194 |  | 52.7636 | 7.9321 | 291.7482 | 0.0018488 |  | 53.6154 | 8.0602 | 296.4581 | 0.0018757 |  | 54.3967 | 8.1776 | 300.7783 | 0.0019005 |  | 55.1159 | 8.2858 | 304.7552
41 |  | Steel | 41 | 0.15033 |  |  | 2.307 | 28.6071 |  |  | 0.0005504 |  | 15.9616 | 2.3996 | 68.6444 |  | 6.8537e-05 |  | 1.9876 | 0.2988 | 8.5478 |  | -0.00072972 |  | -21.1618 | -3.1813 | -91.0085 |  | 0.0005504 |  | 15.9616 | 2.3996 | 68.6444 |  | 0.000763 |  | 22.1269 | 3.3264 | 95.1592 | 0.00093379 |  | 27.0799 | 4.071 | 116.4599 | 0.001074 |  | 31.146 | 4.6823 | 133.9467 | 0.0011912 |  | 34.544 | 5.1931 | 148.5599 | 0.0012905 |  | 37.4259 | 5.6264 | 160.954 | 0.0013759 |  | 39.9011 | 5.9985 | 171.5987 | 0.00145 |  | 42.0499 | 6.3215 | 180.8401 | 0.0015149 |  | 43.933 | 6.6046 | 188.9385 | 0.0015723 |  | 45.5968 | 6.8547 | 196.0936 | 0.0016234 |  | 47.0774 | 7.0773 | 202.4612 | 0.0016691 |  | 48.4035 | 7.2767 | 208.1644 | 0.0017103 |  | 49.5982 | 7.4563 | 213.3021 | 0.0017476 |  | 50.68 | 7.6189 | 217.9545 | 0.0017815 |  | 51.6642 | 7.7668 | 222.1871 | 0.0018125 |  | 52.5634 | 7.902 | 226.0544 | 0.001841 |  | 53.3882 | 8.026 | 229.6017 | 0.0018672 |  | 54.1475 | 8.1402 | 232.8672
42 |  | Steel | 42 | 0.15033 |  |  | 1.6479 | 20.4337 |  |  | 0.00044753 |  | 12.9783 | 1.9511 | 39.8674 |  | -5.9761e-05 |  | -1.7331 | -0.26054 | -5.3238 |  | -0.00090014 |  | -26.1039 | -3.9243 | -80.1876 |  | 0.00044753 |  | 12.9783 | 1.9511 | 39.8674 |  | 0.00067134 |  | 19.469 | 2.9268 | 59.8059 | 0.00085115 |  | 24.6832 | 3.7107 | 75.8235 | 0.00099876 |  | 28.9639 | 4.3542 | 88.9732 | 0.0011221 |  | 32.5412 | 4.892 | 99.9619 | 0.0012267 |  | 35.5752 | 5.3481 | 109.282 | 0.0013166 |  | 38.181 | 5.7399 | 117.2866 | 0.0013946 |  | 40.4432 | 6.08 | 124.2359 | 0.001463 |  | 42.4257 | 6.378 | 130.3257 | 0.0015234 |  | 44.1772 | 6.6413 | 135.7061 | 0.0015771 |  | 45.7359 | 6.8756 | 140.4944 | 0.0016252 |  | 47.132 | 7.0855 | 144.7831 | 0.0016686 |  | 48.3897 | 7.2746 | 148.6465 | 0.0017079 |  | 49.5286 | 7.4458 | 152.145 | 0.0017436 |  | 50.5647 | 7.6016 | 155.3278 | 0.0017763 |  | 51.5114 | 7.7439 | 158.2359 | 0.0018062 |  | 52.3798 | 7.8744 | 160.9034 | 0.0018338 |  | 53.1792 | 7.9946 | 163.3589
43 |  | Steel | 43 | 0.15033 |  |  | 0.98873 | 12.2602 |  |  | 0.00034465 |  | 9.995 | 1.5026 | 18.4219 |  | -0.00018806 |  | -5.4537 | -0.81988 | -10.0519 |  | -0.0010706 |  | -31.0461 | -4.6673 | -57.2215 |  | 0.00034465 |  | 9.995 | 1.5026 | 18.4219 |  | 0.00057969 |  | 16.811 | 2.5272 | 30.9846 | 0.0007685 |  | 22.2866 | 3.3504 | 41.0768 | 0.00092351 |  | 26.7819 | 4.0262 | 49.3621 | 0.001053 |  | 30.5384 | 4.5909 | 56.2858 | 0.0011629 |  | 33.7245 | 5.0699 | 62.1581 | 0.0012573 |  | 36.4608 | 5.4813 | 67.2016 | 0.0013392 |  | 38.8365 | 5.8384 | 71.5802 | 0.001411 |  | 40.9183 | 6.1514 | 75.4172 | 0.0014744 |  | 42.7576 | 6.4279 | 78.8072 | 0.0015308 |  | 44.3945 | 6.674 | 81.8242 | 0.0015814 |  | 45.8606 | 6.8944 | 84.5264 | 0.0016269 |  | 47.1813 | 7.0929 | 86.9606 | 0.0016682 |  | 48.3772 | 7.2727 | 89.1649 | 0.0017057 |  | 49.4653 | 7.4363 | 91.1703 | 0.00174 |  | 50.4595 | 7.5857 | 93.0026 | 0.0017714 |  | 51.3713 | 7.7228 | 94.6834 | 0.0018004 |  | 52.2108 | 7.849 | 96.2305
44 |  | Steel | 44 | 0.15033 |  |  | 0.32958 | 4.0867 |  |  | 0.00024178 |  | 7.0117 | 1.0541 | 4.3078 |  | -0.00031636 |  | -9.1744 | -1.3792 | -5.6365 |  | -0.001241 |  | -35.9882 | -5.4102 | -22.1102 |  | 0.00024178 |  | 7.0117 | 1.0541 | 4.3078 |  | 0.00048803 |  | 14.153 | 2.1277 | 8.6952 | 0.00068586 |  | 19.89 | 2.9901 | 12.2198 | 0.00084827 |  | 24.5998 | 3.6982 | 15.1134 | 0.00098399 |  | 28.5356 | 4.2899 | 17.5315 | 0.0010991 |  | 31.8737 | 4.7917 | 19.5823 | 0.001198 |  | 34.7407 | 5.2227 | 21.3437 | 0.0012838 |  | 37.2298 | 5.5969 | 22.8729 | 0.001359 |  | 39.4109 | 5.9248 | 24.213 | 0.0014254 |  | 41.338 | 6.2145 | 25.3969 | 0.0014846 |  | 43.053 | 6.4723 | 26.4506 | 0.0015376 |  | 44.5891 | 6.7032 | 27.3943 | 0.0015853 |  | 45.9729 | 6.9113 | 28.2444 | 0.0016285 |  | 47.2259 | 7.0996 | 29.0143 | 0.0016678 |  | 48.3659 | 7.271 | 29.7147 | 0.0017037 |  | 49.4075 | 7.4276 | 30.3546 | 0.0017367 |  | 50.3629 | 7.5712 | 30.9416 | 0.001767 |  | 51.2424 | 7.7034 | 31.4819
45 |  | Steel | 45 | 0.15033 |  |  | -0.32958 | -4.0867 |  |  | 0.00013891 |  | 4.0284 | 0.6056 | -2.4749 |  | -0.00044466 |  | -12.895 | -1.9386 | 7.9224 |  | -0.0014114 |  | -40.9304 | -6.1532 | 25.1465 |  | 0.00013891 |  | 4.0284 | 0.6056 | -2.4749 |  | 0.00039638 |  | 11.495 | 1.7281 | -7.0622 | 0.00060322 |  | 17.4933 | 2.6298 | -10.7474 | 0.00077302 |  | 22.4177 | 3.3701 | -13.7728 | 0.00091492 |  | 26.5328 | 3.9888 | -16.301 | 0.0010353 |  | 30.023 | 4.5135 | -18.4453 | 0.0011386 |  | 33.0206 | 4.9641 | -20.2869 | 0.0012284 |  | 35.623 | 5.3553 | -21.8858 | 0.001307 |  | 37.9036 | 5.6982 | -23.2869 | 0.0013765 |  | 39.9185 | 6.0011 | -24.5248 | 0.0014383 |  | 41.7116 | 6.2706 | -25.6264 | 0.0014937 |  | 43.3176 | 6.5121 | -26.6131 | 0.0015436 |  | 44.7644 | 6.7296 | -27.502 | 0.0015888 |  | 46.0745 | 6.9265 | -28.3069 | 0.0016299 |  | 47.2665 | 7.1057 | -29.0392 | 0.0016674 |  | 48.3555 | 7.2694 | -29.7083 | 0.0017019 |  | 49.3544 | 7.4196 | -30.322 | 0.0017336 |  | 50.274 | 7.5579 | -30.8869
46 |  | Steel | 46 | 0.15033 |  |  | -0.98873 | -12.2602 |  |  | 3.6036e-05 |  | 1.045 | 0.15711 | -1.9261 |  | -0.00057295 |  | -16.6157 | -2.4979 | 30.6247 |  | -0.0015818 |  | -45.8725 | -6.8962 | 84.5484 |  | 3.6036e-05 |  | 1.045 | 0.15711 | -1.9261 |  | 0.00030472 |  | 8.837 | 1.3285 | -16.2877 | 0.00052058 |  | 15.0967 | 2.2695 | -27.825 | 0.00069778 |  | 20.2356 | 3.0421 | -37.2966 | 0.00084586 |  | 24.53 | 3.6877 | -45.2117 | 0.00097146 |  | 28.1723 | 4.2352 | -51.9248 | 0.0010793 |  | 31.3005 | 4.7055 | -57.6905 | 0.001173 |  | 34.0163 | 5.1138 | -62.696 | 0.001255 |  | 36.3962 | 5.4716 | -67.0824 | 0.0013275 |  | 38.4989 | 5.7877 | -70.9579 | 0.0013921 |  | 40.3701 | 6.069 | -74.4068 | 0.0014499 |  | 42.0462 | 6.3209 | -77.4959 | 0.0015019 |  | 43.556 | 6.5479 | -80.2787 | 0.0015491 |  | 44.9232 | 6.7535 | -82.7986 | 0.001592 |  | 46.167 | 6.9404 | -85.0912 | 0.0016312 |  | 47.3035 | 7.1113 | -87.1859 | 0.0016671 |  | 48.346 | 7.268 | -89.1073 | 0.0017002 |  | 49.3056 | 7.4123 | -90.876
47 |  | Steel | 47 | 0.15033 |  |  | -1.6479 | -20.4337 |  |  | -6.6836e-05 |  | -1.9383 | -0.29138 | 5.9541 |  | -0.00070125 |  | -20.3363 | -3.0572 | 62.4704 |  | -0.0017522 |  | -50.8147 | -7.6391 | 156.0957 |  | -6.6836e-05 |  | -1.9383 | -0.29138 | 5.9541 |  | 0.00021307 |  | 6.179 | 0.92892 | -18.9812 | 0.00043793 |  | 12.7001 | 1.9092 | -39.0128 | 0.00062254 |  | 18.0535 | 2.714 | -55.4579 | 0.0007768 |  | 22.5272 | 3.3866 | -69.2005 | 0.00090764 |  | 26.3216 | 3.957 | -80.8562 | 0.00102 |  | 29.5804 | 4.4469 | -90.8668 | 0.0011176 |  | 32.4096 | 4.8722 | -99.5577 | 0.0012031 |  | 34.8888 | 5.245 | -107.1736 | 0.0012786 |  | 37.0793 | 5.5743 | -113.9025 | 0.0013458 |  | 39.0287 | 5.8673 | -119.8907 | 0.001406 |  | 40.7747 | 6.1298 | -125.2541 | 0.0014603 |  | 42.3475 | 6.3662 | -130.0858 | 0.0015094 |  | 43.7718 | 6.5804 | -134.4609 | 0.0015541 |  | 45.0676 | 6.7752 | -138.4414 | 0.0015949 |  | 46.2516 | 6.9532 | -142.0784 | 0.0016323 |  | 47.3375 | 7.1164 | -145.4143 | 0.0016668 |  | 48.3372 | 7.2667 | -148.4852
48 |  | Steel | 48 | 0.15033 |  |  | -2.307 | -28.6071 |  |  | -0.00016971 |  | -4.9216 | -0.73987 | 21.1657 |  | -0.00082955 |  | -24.057 | -3.6166 | 103.4597 |  | -0.0019226 |  | -55.7568 | -8.3821 | 239.7882 |  | -0.00016971 |  | -4.9216 | -0.73987 | 21.1657 |  | 0.00012142 |  | 3.5211 | 0.52933 | -15.1427 | 0.00035529 |  | 10.3034 | 1.5489 | -44.311 | 0.00054729 |  | 15.8715 | 2.386 | -68.2568 | 0.00070774 |  | 20.5245 | 3.0855 | -88.2676 | 0.00084382 |  | 24.4709 | 3.6788 | -105.2395 | 0.0009607 |  | 27.8603 | 4.1883 | -119.8161 | 0.0010622 |  | 30.8029 | 4.6307 | -132.4709 | 0.0011511 |  | 33.3815 | 5.0183 | -143.5605 | 0.0012296 |  | 35.6597 | 5.3608 | -153.3584 | 0.0012996 |  | 37.6872 | 5.6656 | -162.0779 | 0.0013622 |  | 39.5032 | 5.9386 | -169.8877 | 0.0014186 |  | 41.1391 | 6.1846 | -176.9231 | 0.0014697 |  | 42.6205 | 6.4073 | -183.2938 | 0.0015161 |  | 43.9682 | 6.6099 | -189.0898 | 0.0015586 |  | 45.1996 | 6.795 | -194.3856 | 0.0015976 |  | 46.3291 | 6.9648 | -199.2431 | 0.0016334 |  | 47.3688 | 7.1211 | -203.7147
49 |  | Steel | 49 | 0.15033 |  |  | -2.9662 | -36.7806 |  |  | -0.00027258 |  | -7.9049 | -1.1884 | 43.7088 |  | -0.00095785 |  | -27.7777 | -4.1759 | 153.5924 |  | -0.0020931 |  | -60 | -9.02 | 331.7609 |  | -0.00027258 |  | -7.9049 | -1.1884 | 43.7088 |  | 2.9761e-05 |  | 0.86308 | 0.12975 | -4.7722 | 0.00027265 |  | 7.9068 | 1.1887 | -43.7194 | 0.00047205 |  | 13.6894 | 2.058 | -75.6933 | 0.00063868 |  | 18.5217 | 2.7844 | -102.4127 | 0.00078001 |  | 22.6201 | 3.4006 | -125.0747 | 0.00090139 |  | 26.1402 | 3.9297 | -144.5381 | 0.0010068 |  | 29.1961 | 4.3892 | -161.4356 | 0.0010991 |  | 31.8741 | 4.7917 | -176.2431 | 0.0011807 |  | 34.2402 | 5.1474 | -189.3258 | 0.0012533 |  | 36.3458 | 5.464 | -200.9685 | 0.0013183 |  | 38.2317 | 5.7475 | -211.3966 | 0.0013769 |  | 39.9307 | 6.0029 | -220.7906 | 0.00143 |  | 41.4691 | 6.2342 | -229.2972 | 0.0014782 |  | 42.8688 | 6.4446 | -237.0364 | 0.0015223 |  | 44.1476 | 6.6369 | -244.1076 | 0.0015628 |  | 45.3206 | 6.8132 | -250.5936 | 0.0016 |  | 46.4005 | 6.9755 | -256.5643
50 |  | Steel | 50 | 0.15033 |  |  | -3.6253 | -44.9541 |  |  | -0.00037545 |  | -10.8882 | -1.6369 | 73.5833 |  | -0.0010861 |  | -31.4983 | -4.7352 | 212.8685 |  | -0.0022635 |  | -60 | -9.02 | 405.4856 |  | -0.00037545 |  | -10.8882 | -1.6369 | 73.5833 |  | -6.1893e-05 |  | -1.7949 | -0.26983 | 12.1301 | 0.00019001 |  | 5.5102 | 0.82836 | -37.2382 | 0.0003968 |  | 11.5073 | 1.7299 | -77.7673 | 0.00056962 |  | 16.5189 | 2.4833 | -111.6361 | 0.00071619 |  | 20.7694 | 3.1223 | -140.3617 | 0.00084207 |  | 24.4201 | 3.6711 | -165.033 | 0.00095136 |  | 27.5894 | 4.1476 | -186.4517 | 0.0010471 |  | 30.3667 | 4.5651 | -205.2213 | 0.0011317 |  | 32.8206 | 4.934 | -221.8046 | 0.001207 |  | 35.0043 | 5.2623 | -236.5625 | 0.0012745 |  | 36.9603 | 5.5564 | -249.7808 | 0.0013352 |  | 38.7222 | 5.8212 | -261.6885 | 0.0013903 |  | 40.3178 | 6.0611 | -272.4712 | 0.0014403 |  | 41.7694 | 6.2793 | -282.2812 | 0.0014861 |  | 43.0956 | 6.4787 | -291.2444 | 0.001528 |  | 44.3122 | 6.6616 | -299.4659 | 0.0015666 |  | 45.4321 | 6.83 | -307.0342
51 |  | Steel | 51 | 0.15033 |  |  | -4.2845 | -53.1275 |  |  | -0.00047833 |  | -13.8715 | -2.0853 | 110.7892 |  | -0.0012144 |  | -35.219 | -5.2946 | 281.2881 |  | -0.0024339 |  | -60 | -9.02 | 479.2102 |  | -0.00047833 |  | -13.8715 | -2.0853 | 110.7892 |  | -0.00015355 |  | -4.4529 | -0.66942 | 35.5645 | 0.00010736 |  | 3.1135 | 0.46807 | -24.8672 | 0.00032156 |  | 9.3252 | 1.4019 | -74.4789 | 0.00050055 |  | 14.5161 | 2.1823 | -115.9377 | 0.00065237 |  | 18.9187 | 2.8441 | -151.1007 | 0.00078276 |  | 22.6999 | 3.4126 | -181.3007 | 0.00089595 |  | 25.9827 | 3.9061 | -207.5194 | 0.00099515 |  | 28.8594 | 4.3385 | -230.4952 | 0.0010828 |  | 31.401 | 4.7206 | -250.7948 | 0.0011608 |  | 33.6629 | 5.0607 | -268.86 | 0.0012306 |  | 35.6888 | 5.3652 | -285.0405 | 0.0012936 |  | 37.5138 | 5.6396 | -299.6166 | 0.0013506 |  | 39.1664 | 5.888 | -312.8157 | 0.0014024 |  | 40.6699 | 6.114 | -324.8241 | 0.0014498 |  | 42.0437 | 6.3206 | -335.796 | 0.0014932 |  | 43.3037 | 6.51 | -345.8599 | 0.0015332 |  | 44.4637 | 6.6844 | -355.1243
52 |  | Steel | 52 | 0.15033 |  |  | -4.9436 | -61.301 |  |  | -0.0005812 |  | -16.8548 | -2.5338 | 155.3266 |  | -0.0013427 |  | -38.9396 | -5.8539 | 358.8512 |  | -0.0026043 |  | -60 | -9.02 | 552.9349 |  | -0.0005812 |  | -16.8548 | -2.5338 | 155.3266 |  | -0.0002452 |  | -7.1109 | -1.069 | 65.5308 | 2.472e-05 |  | 0.71689 | 0.10777 | -6.6066 | 0.00024631 |  | 7.1431 | 1.0738 | -65.828 | 0.00043149 |  | 12.5133 | 1.8812 | -115.3174 | 0.00058855 |  | 17.068 | 2.5659 | -157.2915 | 0.00072344 |  | 20.9798 | 3.154 | -193.3413 | 0.00084055 |  | 24.3759 | 3.6645 | -224.6385 | 0.00094317 |  | 27.352 | 4.1119 | -252.0647 | 0.0010338 |  | 29.9814 | 4.5072 | -276.2964 | 0.0011145 |  | 32.3214 | 4.859 | -297.8608 | 0.0011868 |  | 34.4173 | 5.1741 | -317.1755 | 0.0012519 |  | 36.3054 | 5.4579 | -334.575 | 0.0013109 |  | 38.0151 | 5.7149 | -350.3308 | 0.0013645 |  | 39.5705 | 5.9488 | -364.6652 | 0.0014135 |  | 40.9917 | 6.1624 | -377.7623 | 0.0014585 |  | 42.2953 | 6.3584 | -389.7757 | 0.0014998 |  | 43.4953 | 6.5388 | -400.8345
53 |  | Steel | 53 | 0.15033 |  |  | -5.6028 | -69.4744 |  |  | -0.00068407 |  | -19.8381 | -2.9823 | 207.1954 |  | -0.001471 |  | -42.6603 | -6.4133 | 445.5578 |  | -0.0027747 |  | -60 | -9.02 | 626.6595 |  | -0.00068407 |  | -19.8381 | -2.9823 | 207.1954 |  | -0.00033686 |  | -9.7689 | -1.4686 | 102.0291 | -5.7922e-05 |  | -1.6797 | -0.25252 | 17.5438 | 0.00017107 |  | 4.961 | 0.74581 | -51.8147 | 0.00036243 |  | 10.5105 | 1.5801 | -109.7753 | 0.00052473 |  | 15.2173 | 2.2877 | -158.9342 | 0.00066413 |  | 19.2597 | 2.8954 | -201.1548 | 0.00078515 |  | 22.7692 | 3.423 | -237.8091 | 0.00089119 |  | 25.8447 | 3.8853 | -269.93 | 0.00098489 |  | 28.5619 | 4.2938 | -298.3094 | 0.0010683 |  | 30.98 | 4.6573 | -323.5651 | 0.001143 |  | 33.1458 | 4.9829 | -346.1859 | 0.0012102 |  | 35.0969 | 5.2762 | -366.5637 | 0.0012712 |  | 36.8637 | 5.5418 | -385.0164 | 0.0013266 |  | 38.4711 | 5.7835 | -401.8045 | 0.0013772 |  | 39.9397 | 6.0043 | -417.1435 | 0.0014237 |  | 41.2868 | 6.2068 | -431.2132 | 0.0014664 |  | 42.5269 | 6.3932 | -444.165
54 |  | Steel | 54 | 0.15033 |  |  | -6.2619 | -77.6479 |  |  | -0.00078694 |  | -22.8214 | -3.4308 | 266.3956 |  | -0.0015993 |  | -46.3809 | -6.9726 | 541.4078 |  | -0.0029452 |  | -60 | -9.02 | 700.3842 |  | -0.00078694 |  | -22.8214 | -3.4308 | 266.3956 |  | -0.00042851 |  | -12.4268 | -1.8682 | 145.0593 | -0.00014056 |  | -4.0764 | -0.61282 | 47.5839 | 9.5826e-05 |  | 2.779 | 0.41777 | -32.439 | 0.00029337 |  | 8.5077 | 1.279 | -99.3114 | 0.00046092 |  | 13.3666 | 2.0094 | -156.0287 | 0.00060481 |  | 17.5396 | 2.6368 | -204.741 | 0.00072974 |  | 21.1625 | 3.1814 | -247.0312 | 0.00083922 |  | 24.3373 | 3.6587 | -284.0909 | 0.00093594 |  | 27.1423 | 4.0804 | -316.8338 | 0.001022 |  | 29.6385 | 4.4557 | -345.9727 | 0.0010991 |  | 31.8744 | 4.7918 | -372.0717 | 0.0011686 |  | 33.8885 | 5.0946 | -395.5827 | 0.0012315 |  | 35.7123 | 5.3688 | -416.8727 | 0.0012887 |  | 37.3717 | 5.6182 | -436.242 | 0.001341 |  | 38.8878 | 5.8461 | -453.9395 | 0.0013889 |  | 40.2784 | 6.0552 | -470.1725 | 0.0014331 |  | 41.5585 | 6.2476 | -485.1157
55 |  | Steel | 55 | 0.15033 |  |  | -6.9211 | -85.8214 |  |  | -0.00088982 |  | -25.8047 | -3.8793 | 332.9273 |  | -0.0017276 |  | -50.1016 | -7.5319 | 646.4013 |  | -0.0031156 |  | -60 | -9.02 | 774.1088 |  | -0.00088982 |  | -25.8047 | -3.8793 | 332.9273 |  | -0.00052017 |  | -15.0848 | -2.2678 | 194.6215 | -0.00022321 |  | -6.473 | -0.97311 | 83.5136 | 2.0582e-05 |  | 0.59688 | 0.089731 | -7.7008 | 0.00022431 |  | 6.5049 | 0.97791 | -83.9256 | 0.0003971 |  | 11.5158 | 1.7312 | -148.5752 | 0.0005455 |  | 15.8195 | 2.3782 | -204.1001 | 0.00067434 |  | 19.5558 | 2.9399 | -252.3049 | 0.00078724 |  | 22.8299 | 3.4321 | -294.5475 | 0.00088699 |  | 25.7227 | 3.867 | -331.8696 | 0.00097576 |  | 28.2971 | 4.254 | -365.0838 | 0.0010553 |  | 30.6029 | 4.6006 | -394.8328 | 0.0011269 |  | 32.6801 | 4.9129 | -421.632 | 0.0011918 |  | 34.561 | 5.1957 | -445.8994 | 0.0012508 |  | 36.2722 | 5.4529 | -467.9777 | 0.0013047 |  | 37.8358 | 5.688 | -488.1502 | 0.0013541 |  | 39.2699 | 5.9036 | -506.6535 | 0.0013997 |  | 40.5902 | 6.1021 | -523.6866
56 |  | Steel | 56 | 0.15033 |  |  | -7.5802 | -93.9948 |  |  | -0.00099269 |  | -28.788 | -4.3278 | 406.7904 |  | -0.0018559 |  | -53.8222 | -8.0913 | 760.5383 |  | -0.003286 |  | -60 | -9.02 | 847.8335 |  | -0.00099269 |  | -28.788 | -4.3278 | 406.7904 |  | -0.00061182 |  | -17.7428 | -2.6673 | 250.7157 | -0.00030585 |  | -8.8697 | -1.3334 | 125.3331 | -5.4662e-05 |  | -1.5852 | -0.23831 | 22.3998 | 0.00015525 |  | 4.5022 | 0.67682 | -63.618 | 0.00033328 |  | 9.6651 | 1.453 | -136.5735 | 0.00048619 |  | 14.0994 | 2.1196 | -199.2321 | 0.00061893 |  | 17.949 | 2.6983 | -253.6299 | 0.00073526 |  | 21.3226 | 3.2055 | -301.2997 | 0.00083804 |  | 24.3031 | 3.6536 | -343.4169 | 0.0009295 |  | 26.9556 | 4.0523 | -380.8983 | 0.0010114 |  | 29.3314 | 4.4095 | -414.4693 | 0.0010852 |  | 31.4716 | 4.7312 | -444.7115 | 0.0011521 |  | 33.4096 | 5.0226 | -472.0967 | 0.0012129 |  | 35.1728 | 5.2876 | -497.0115 | 0.0012684 |  | 36.7838 | 5.5298 | -519.7757 | 0.0013194 |  | 38.2615 | 5.752 | -540.6563 | 0.0013663 |  | 39.6218 | 5.9565 | -559.8777
57 |  | Steel | 57 | 0.15033 |  |  | -8.2394 | -102.1683 |  |  | -0.0010956 |  | -31.7713 | -4.7763 | 487.9849 |  | -0.0019842 |  | -57.5429 | -8.6506 | 883.8187 |  | -0.0034564 |  | -60 | -9.02 | 921.5581 |  | -0.0010956 |  | -31.7713 | -4.7763 | 487.9849 |  | -0.00070348 |  | -20.4008 | -3.0669 | 313.3418 | -0.00038849 |  | -11.2663 | -1.6937 | 173.0423 | -0.00012991 |  | -3.7673 | -0.56635 | 57.8629 | 8.6185e-05 |  | 2.4994 | 0.37574 | -38.3887 | 0.00026946 |  | 7.8144 | 1.1748 | -120.0237 | 0.00042687 |  | 12.3793 | 1.861 | -190.1369 | 0.00056353 |  | 16.3423 | 2.4568 | -251.0065 | 0.00068328 |  | 19.8152 | 2.9789 | -304.3476 | 0.00078909 |  | 22.8836 | 3.4402 | -351.4755 | 0.00088325 |  | 25.6142 | 3.8507 | -393.4161 | 0.00096758 |  | 28.0599 | 4.2183 | -430.9811 | 0.0010436 |  | 30.2632 | 4.5496 | -464.8213 | 0.0011124 |  | 32.2583 | 4.8495 | -495.4646 | 0.0011749 |  | 34.0734 | 5.1224 | -523.3435 | 0.0012321 |  | 35.7318 | 5.3717 | -548.816 | 0.0012846 |  | 37.253 | 5.6004 | -572.1808 | 0.0013329 |  | 38.6534 | 5.8109 | -593.689
58 |  | Steel | 58 | 0.15033 |  |  | -8.8985 | -110.3418 |  |  | -0.0011984 |  | -34.7546 | -5.2248 | 576.5109 |  | -0.0021125 |  | -60 | -9.02 | 995.2828 |  | -0.0036268 |  | -60 | -9.02 | 995.2828 |  | -0.0011984 |  | -34.7546 | -5.2248 | 576.5109 |  | -0.00079513 |  | -23.0588 | -3.4665 | 382.4998 | -0.00047114 |  | -13.6629 | -2.054 | 226.6412 | -0.00020515 |  | -5.9494 | -0.89439 | 98.6884 | 1.7124e-05 |  | 0.49659 | 0.074654 | -8.2374 | 0.00020564 |  | 5.9637 | 0.89654 | -98.9258 | 0.00036756 |  | 10.6592 | 1.6024 | -176.8145 | 0.00050812 |  | 14.7356 | 2.2152 | -244.4346 | 0.0006313 |  | 18.3078 | 2.7523 | -303.6912 | 0.00074014 |  | 21.464 | 3.2268 | -356.0456 | 0.00083699 |  | 24.2727 | 3.649 | -402.6374 | 0.00092374 |  | 26.7885 | 4.0272 | -444.3684 | 0.0010019 |  | 29.0547 | 4.3679 | -481.9614 | 0.0010727 |  | 31.1069 | 4.6764 | -516.0031 | 0.001137 |  | 32.974 | 4.9571 | -546.9737 | 0.0011959 |  | 34.6799 | 5.2135 | -575.2711 | 0.0012498 |  | 36.2446 | 5.4488 | -601.227 | 0.0012995 |  | 37.685 | 5.6653 | -625.1205
59 |  | Steel | 59 | 0.15033 |  |  | -9.5577 | -118.5152 |  |  | -0.0013013 |  | -37.7379 | -5.6733 | 672.3683 |  | -0.0022408 |  | -60 | -9.02 | 1069.0074 |  | -0.0037973 |  | -60 | -9.02 | 1069.0074 |  | -0.0013013 |  | -37.7379 | -5.6733 | 672.3683 |  | -0.00088678 |  | -25.7167 | -3.8661 | 458.1899 | -0.00055378 |  | -16.0596 | -2.4143 | 286.1298 | -0.00028039 |  | -8.1314 | -1.2224 | 144.8763 | -5.1938e-05 |  | -1.5062 | -0.22643 | 26.8356 | 0.00014183 |  | 4.113 | 0.61832 | -73.2798 | 0.00030824 |  | 8.939 | 1.3438 | -159.265 | 0.00045272 |  | 13.1289 | 1.9737 | -233.9142 | 0.00057933 |  | 16.8005 | 2.5257 | -299.3305 | 0.00069119 |  | 20.0444 | 3.0133 | -357.1271 | 0.00079073 |  | 22.9313 | 3.4473 | -408.5621 | 0.0008799 |  | 25.517 | 3.8361 | -454.6309 | 0.00096022 |  | 27.8463 | 4.1862 | -496.1318 | 0.001033 |  | 29.9556 | 4.5033 | -533.7121 | 0.0010991 |  | 31.8745 | 4.7918 | -567.9021 | 0.0011596 |  | 33.6279 | 5.0554 | -599.141 | 0.001215 |  | 35.2361 | 5.2972 | -627.795 | 0.0012661 |  | 36.7166 | 5.5197 | -654.1722
60 |  | Steel | 60 | 0.15033 |  |  | -10.2168 | -126.6887 |  |  | -0.0014042 |  | -40.7212 | -6.1218 | 775.5571 |  | -0.0023691 |  | -60 | -9.02 | 1142.7321 |  | -0.0039677 |  | -60 | -9.02 | 1142.7321 |  | -0.0014042 |  | -40.7212 | -6.1218 | 775.5571 |  | -0.00097844 |  | -28.3747 | -4.2657 | 540.4119 | -0.00063642 |  | -18.4562 | -2.7746 | 351.5081 | -0.00035564 |  | -10.3135 | -1.5505 | 196.4267 | -0.000121 |  | -3.509 | -0.52752 | 66.8305 | 7.8008e-05 |  | 2.2622 | 0.34009 | -43.0857 | 0.00024893 |  | 7.2189 | 1.0852 | -137.4883 | 0.00039731 |  | 11.5221 | 1.7322 | -219.4452 | 0.00052735 |  | 15.2931 | 2.2991 | -291.2654 | 0.00064224 |  | 18.6248 | 2.7999 | -354.72 | 0.00074448 |  | 21.5898 | 3.2457 | -411.1902 | 0.00083605 |  | 24.2455 | 3.6449 | -461.7689 | 0.00091855 |  | 26.6379 | 4.0046 | -507.3325 | 0.00099325 |  | 28.8042 | 4.3302 | -548.5916 | 0.0010612 |  | 30.7751 | 4.6265 | -586.1287 | 0.0011233 |  | 32.5759 | 4.8972 | -620.4257 | 0.0011803 |  | 34.2277 | 5.1456 | -651.8848 | 0.0012327 |  | 35.7482 | 5.3742 | -680.8441
61 |  | Steel | 61 | 0.15033 |  |  | -10.876 | -134.8622 |  |  | -0.0015071 |  | -43.7045 | -6.5702 | 886.0774 |  | -0.0024974 |  | -60 | -9.02 | 1216.4567 |  | -0.0041381 |  | -60 | -9.02 | 1216.4567 |  | -0.0015071 |  | -43.7045 | -6.5702 | 886.0774 |  | -0.0010701 |  | -31.0327 | -4.6653 | 629.1658 | -0.00071906 |  | -20.8528 | -3.1349 | 422.7761 | -0.00043088 |  | -12.4956 | -1.8785 | 253.3395 | -0.00019006 |  | -5.5118 | -0.8286 | 111.7472 | 1.4191e-05 |  | 0.41153 | 0.061866 | -8.3434 | 0.00018961 |  | 5.4988 | 0.82665 | -111.4845 | 0.00034191 |  | 9.9154 | 1.4906 | -201.0277 | 0.00047537 |  | 13.7857 | 2.0725 | -279.496 | 0.00059328 |  | 17.2053 | 2.5865 | -348.8243 | 0.00069822 |  | 20.2484 | 3.044 | -410.5217 | 0.00079221 |  | 22.974 | 3.4538 | -465.7822 | 0.00087688 |  | 25.4294 | 3.8229 | -515.5634 | 0.00095355 |  | 27.6529 | 4.1571 | -560.6417 | 0.0010233 |  | 29.6757 | 4.4612 | -601.6535 | 0.001087 |  | 31.5239 | 4.7391 | -639.1252 | 0.0011455 |  | 33.2192 | 4.994 | -673.4962 | 0.0011993 |  | 34.7798 | 5.2286 | -705.1362
62 |  | Steel | 62 | 0.15033 |  |  | -11.5351 | -143.0356 |  |  | -0.0016099 |  | -46.6878 | -7.0187 | 1003.9291 |  | -0.0026257 |  | -60 | -9.02 | 1290.1814 |  | -0.0043085 |  | -60 | -9.02 | 1290.1814 |  | -0.0016099 |  | -46.6878 | -7.0187 | 1003.9291 |  | -0.0011617 |  | -33.6907 | -5.0648 | 724.4518 | -0.00080171 |  | -23.2495 | -3.4952 | 499.9338 | -0.00050613 |  | -14.6777 | -2.2065 | 315.6148 | -0.00025912 |  | -7.5146 | -1.1297 | 161.5857 | -4.9627e-05 |  | -1.4392 | -0.21636 | 30.9469 | 0.0001303 |  | 3.7787 | 0.56806 | -81.2535 | 0.00028651 |  | 8.3087 | 1.2491 | -178.6618 | 0.00042339 |  | 12.2784 | 1.8458 | -264.0223 | 0.00054433 |  | 15.7857 | 2.3731 | -339.44 | 0.00065196 |  | 18.9069 | 2.8423 | -406.5565 | 0.00074836 |  | 21.7026 | 3.2626 | -466.6709 | 0.00083521 |  | 24.221 | 3.6412 | -520.8247 | 0.00091384 |  | 26.5015 | 3.9841 | -569.8624 | 0.00098539 |  | 28.5763 | 4.296 | -614.4764 | 0.0010508 |  | 30.472 | 4.581 | -655.2394 | 0.0011107 |  | 32.2108 | 4.8424 | -692.6295 | 0.0011659 |  | 33.8115 | 5.083 | -727.0486
63 |  | Steel | 63 | 0.15033 |  |  | -12.1943 | -151.2091 |  |  | -0.0017128 |  | -49.6711 | -7.4672 | 1129.1123 |  | -0.002754 |  | -60 | -9.02 | 1363.906 |  | -0.0044789 |  | -60 | -9.02 | 1363.906 |  | -0.0017128 |  | -49.6711 | -7.4672 | 1129.1123 |  | -0.0012534 |  | -36.3487 | -5.4644 | 826.2696 | -0.00088435 |  | -25.6461 | -3.8555 | 582.9812 | -0.00058137 |  | -16.8598 | -2.5346 | 383.2525 | -0.00032818 |  | -9.5173 | -1.4308 | 216.346 | -0.00011345 |  | -3.2899 | -0.49458 | 74.7854 | 7.0986e-05 |  | 2.0586 | 0.30947 | -46.7953 | 0.0002311 |  | 6.702 | 1.0075 | -152.3473 | 0.00037141 |  | 10.771 | 1.6192 | -244.8442 | 0.00049538 |  | 14.3661 | 2.1597 | -326.5671 | 0.00060571 |  | 17.5655 | 2.6407 | -399.2948 | 0.00070452 |  | 20.4311 | 3.0715 | -464.435 | 0.00079354 |  | 23.0126 | 3.4596 | -523.1162 | 0.00087414 |  | 25.3501 | 3.811 | -576.2536 | 0.00094748 |  | 27.4769 | 4.1307 | -624.5975 | 0.0010145 |  | 29.42 | 4.4228 | -668.7685 | 0.0010759 |  | 31.2023 | 4.6908 | -709.2845 | 0.0011325 |  | 32.8431 | 4.9374 | -746.5811
64 |  | Steel | 64 | 0.15033 |  |  | -12.8534 | -159.3826 |  |  | -0.0018157 |  | -52.6544 | -7.9157 | 1261.6268 |  | -0.0028823 |  | -60 | -9.02 | 1437.6307 |  | -0.0046494 |  | -60 | -9.02 | 1437.6307 |  | -0.0018157 |  | -52.6544 | -7.9157 | 1261.6268 |  | -0.0013451 |  | -39.0067 | -5.864 | 934.6195 | -0.00096699 |  | -28.0427 | -4.2158 | 671.9183 | -0.00065662 |  | -19.0419 | -2.8626 | 456.2526 | -0.00039725 |  | -11.5201 | -1.7319 | 276.0282 | -0.00017726 |  | -5.1406 | -0.77281 | 123.172 | 1.1671e-05 |  | 0.33847 | 0.050884 | -8.11 | 0.0001757 |  | 5.0952 | 0.76598 | -122.0843 | 0.00031944 |  | 9.2637 | 1.3926 | -221.9619 | 0.00044643 |  | 12.9465 | 1.9463 | -310.2057 | 0.00055945 |  | 16.2241 | 2.439 | -388.7366 | 0.00066068 |  | 19.1596 | 2.8803 | -459.0745 | 0.00075187 |  | 21.8041 | 3.2779 | -522.438 | 0.00083444 |  | 24.1988 | 3.6379 | -579.8154 | 0.00090957 |  | 26.3774 | 3.9654 | -632.0168 | 0.00097821 |  | 28.368 | 4.2647 | -679.7123 | 0.0010412 |  | 30.1939 | 4.5391 | -723.4612 | 0.0010991 |  | 31.8747 | 4.7918 | -763.7338
65 |  | Steel | 65 | 0.22 |  |  | -13.3438 | -165.4628 |  |  | -0.0018922 |  | -54.8737 | -12.0722 | 1997.5028 |  | -0.0029778 |  | -60 | -13.2 | 2184.1092 |  | -0.0047761 |  | -60 | -13.2 | 2184.1092 |  | -0.0018922 |  | -54.8737 | -12.0722 | 1997.5028 |  | -0.0014132 |  | -40.9839 | -9.0165 | 1491.8899 | -0.0010285 |  | -29.8256 | -6.5616 | 1085.706 | -0.00071259 |  | -20.6651 | -4.5463 | 752.2477 | -0.00044862 |  | -13.01 | -2.8622 | 473.588 | -0.00022474 |  | -6.5174 | -1.4338 | 237.2445 | -3.2453e-05 |  | -0.94112 | -0.20705 | 34.2586 | 0.00013448 |  | 3.9 | 0.858 | -141.9664 | 0.00028077 |  | 8.1423 | 1.7913 | -296.3953 | 0.00041002 |  | 11.8905 | 2.6159 | -432.8363 | 0.00052504 |  | 15.2261 | 3.3498 | -554.2593 | 0.00062806 |  | 18.2138 | 4.007 | -663.0146 | 0.00072087 |  | 20.9052 | 4.5991 | -760.9861 | 0.00080491 |  | 23.3423 | 5.1353 | -849.702 | 0.00088136 |  | 25.5596 | 5.6231 | -930.4149 | 0.00095122 |  | 27.5855 | 6.0688 | -1004.1608 | 0.0010153 |  | 29.4437 | 6.4776 | -1071.8045 | 0.0010743 |  | 31.1543 | 6.8539 | -1134.0734
66 |  | Steel | 66 | 0.22 |  |  | -13.6653 | -169.4499 |  |  | -0.0019424 |  | -56.329 | -12.3924 | 2099.8864 |  | -0.0030404 |  | -60 | -13.2 | 2236.7383 |  | -0.0048593 |  | -60 | -13.2 | 2236.7383 |  | -0.0019424 |  | -56.329 | -12.3924 | 2099.8864 |  | -0.0014579 |  | -42.2805 | -9.3017 | 1576.1741 | -0.0010688 |  | -30.9947 | -6.8188 | 1155.4501 | -0.00074929 |  | -21.7295 | -4.7805 | 810.055 | -0.00048231 |  | -13.987 | -3.0771 | 521.4201 | -0.00025587 |  | -7.4202 | -1.6324 | 276.6163 | -6.1386e-05 |  | -1.7802 | -0.39164 | 66.3641 | 0.00010746 |  | 3.1162 | 0.68557 | -116.1692 | 0.00025541 |  | 7.407 | 1.6295 | -276.1262 | 0.00038614 |  | 11.198 | 2.4636 | -417.4513 | 0.00050248 |  | 14.5718 | 3.2058 | -543.2209 | 0.00060667 |  | 17.5935 | 3.8706 | -655.8692 | 0.00070054 |  | 20.3157 | 4.4695 | -757.3478 | 0.00078554 |  | 22.7807 | 5.0117 | -849.2396 | 0.00086287 |  | 25.0233 | 5.5051 | -932.8417 | 0.00093353 |  | 27.0723 | 5.9559 | -1009.2275 | 0.00099834 |  | 28.9518 | 6.3694 | -1079.2926 | 0.001058 |  | 30.6819 | 6.75 | -1143.7905
67 |  | Steel | 67 | 0.22 |  |  | -13.9868 | -173.4369 |  |  | -0.0019926 |  | -57.7842 | -12.7125 | 2204.823 |  | -0.0031029 |  | -60 | -13.2 | 2289.3675 |  | -0.0049424 |  | -60 | -13.2 | 2289.3675 |  | -0.0019926 |  | -57.7842 | -12.7125 | 2204.823 |  | -0.0015027 |  | -43.5771 | -9.587 | 1662.7329 | -0.0011091 |  | -32.1638 | -7.076 | 1227.2452 | -0.000786 |  | -22.794 | -5.0147 | 869.7297 | -0.000516 |  | -14.9639 | -3.2921 | 570.9662 | -0.000287 |  | -8.323 | -1.8311 | 317.5719 | -9.032e-05 |  | -2.6193 | -0.57624 | 99.9417 | 8.0429e-05 |  | 2.3324 | 0.51314 | -88.997 | 0.00023006 |  | 6.6717 | 1.4678 | -254.5671 | 0.00036226 |  | 10.5056 | 2.3112 | -400.8516 | 0.00047991 |  | 13.9174 | 3.0618 | -531.0346 | 0.00058529 |  | 16.9733 | 3.7341 | -647.6358 | 0.00068021 |  | 19.7262 | 4.3398 | -752.6755 | 0.00076617 |  | 22.219 | 4.8882 | -847.7918 | 0.00084438 |  | 24.487 | 5.3871 | -934.3276 | 0.00091583 |  | 26.5591 | 5.843 | -1013.3939 | 0.00098137 |  | 28.4599 | 6.2612 | -1085.9177 | 0.0010417 |  | 30.2095 | 6.6461 | -1152.6789
68 |  | Steel | 68 | 0.22 |  |  | -14.3084 | -177.424 |  |  | -0.0020427 |  | -59.2395 | -13.0327 | 2312.3125 |  | -0.0031655 |  | -60 | -13.2 | 2341.9966 |  | -0.0050255 |  | -60 | -13.2 | 2341.9966 |  | -0.0020427 |  | -59.2395 | -13.0327 | 2312.3125 |  | -0.0015474 |  | -44.8737 | -9.8722 | 1751.5663 | -0.0011494 |  | -33.3329 | -7.3332 | 1301.0911 | -0.0008227 |  | -23.8584 | -5.2488 | 931.2716 | -0.00054969 |  | -15.9409 | -3.507 | 622.2261 | -0.00031813 |  | -9.2257 | -2.0297 | 360.1112 | -0.00011925 |  | -3.4584 | -0.76084 | 134.9912 | 5.3403e-05 |  | 1.5487 | 0.34071 | -60.4498 | 0.0002047 |  | 5.9364 | 1.306 | -231.7181 | 0.00033838 |  | 9.8131 | 2.1589 | -383.0369 | 0.00045735 |  | 13.263 | 2.9179 | -517.7002 | 0.0005639 |  | 16.3531 | 3.5977 | -638.3144 | 0.00065989 |  | 19.1367 | 4.2101 | -746.969 | 0.00074681 |  | 21.6574 | 4.7646 | -845.3587 | 0.00082588 |  | 23.9507 | 5.2691 | -934.8727 | 0.00089814 |  | 26.046 | 5.7301 | -1016.6601 | 0.00096441 |  | 27.9679 | 6.1529 | -1091.6799 | 0.0010254 |  | 29.7372 | 6.5422 | -1160.7387
69 |  | Steel | 69 | 0.0465 |  |  | -52.224 | -172.3598 |  |  | -0.001979 |  | -57.3911 | -2.6687 | 459.9741 |  | -0.003086 |  | -60 | -2.79 | 480.8838 |  | -0.0049199 |  | -60 | -2.79 | 480.8838 |  | -0.001979 |  | -57.3911 | -2.6687 | 459.9741 |  | -0.0014906 |  | -43.2268 | -2.01 | 346.4512 | -0.0010982 |  | -31.8479 | -1.4809 | 255.2526 | -0.00077608 |  | -22.5064 | -1.0465 | 180.3828 | -0.0005069 |  | -14.7 | -0.68355 | 117.8166 | -0.00027859 |  | -8.0791 | -0.37568 | 64.7515 | -8.2503e-05 |  | -2.3926 | -0.11126 | 19.176 | 8.7731e-05 |  | 2.5442 | 0.1183 | -20.391 | 0.00023691 |  | 6.8704 | 0.31947 | -55.0642 | 0.00036871 |  | 10.6926 | 0.49721 | -85.6986 | 0.00048601 |  | 14.0942 | 0.65538 | -112.9612 | 0.00059106 |  | 17.1409 | 0.79705 | -137.3795 | 0.00068571 |  | 19.8855 | 0.92467 | -159.3766 | 0.00077141 |  | 22.3708 | 1.0402 | -179.2956 | 0.00084937 |  | 24.6319 | 1.1454 | -197.4176 | 0.00092061 |  | 26.6978 | 1.2414 | -213.9755 | 0.00098596 |  | 28.5928 | 1.3296 | -229.1632 | 0.0010461 |  | 30.3372 | 1.4107 | -243.1441
70 |  | Steel | 70 | 0.0465 |  |  | -48.6357 | -172.6492 |  |  | -0.0019826 |  | -57.4967 | -2.6736 | 461.5943 |  | -0.0030906 |  | -60 | -2.79 | 481.6912 |  | -0.004926 |  | -60 | -2.79 | 481.6912 |  | -0.0019826 |  | -57.4967 | -2.6736 | 461.5943 |  | -0.0014938 |  | -43.3209 | -2.0144 | 347.7883 | -0.0011011 |  | -31.9328 | -1.4849 | 256.3624 | -0.00077875 |  | -22.5837 | -1.0501 | 181.3058 | -0.00050934 |  | -14.7709 | -0.68685 | 118.5837 | -0.00028085 |  | -8.1446 | -0.37872 | 65.3862 | -8.4603e-05 |  | -2.4535 | -0.11409 | 19.6971 | 8.5769e-05 |  | 2.4873 | 0.11566 | -19.9685 | 0.00023507 |  | 6.817 | 0.31699 | -54.7282 | 0.00036698 |  | 10.6424 | 0.49487 | -85.439 | 0.00048437 |  | 14.0467 | 0.65317 | -112.7695 | 0.00058951 |  | 17.0959 | 0.79496 | -137.2487 | 0.00068423 |  | 19.8427 | 0.92268 | -159.3007 | 0.00077 |  | 22.33 | 1.0383 | -179.2693 | 0.00084803 |  | 24.5929 | 1.1436 | -197.4366 | 0.00091933 |  | 26.6605 | 1.2397 | -214.0357 | 0.00098473 |  | 28.557 | 1.3279 | -229.2613 | 0.0010449 |  | 30.3029 | 1.4091 | -243.2771
71 |  | Steel | 71 | 0.0465 |  |  | -45.0473 | -172.9385 |  |  | -0.0019863 |  | -57.6023 | -2.6785 | 463.2174 |  | -0.0030951 |  | -60 | -2.79 | 482.4985 |  | -0.004932 |  | -60 | -2.79 | 482.4985 |  | -0.0019863 |  | -57.6023 | -2.6785 | 463.2174 |  | -0.0014971 |  | -43.415 | -2.0188 | 349.1281 | -0.0011041 |  | -32.0176 | -1.4888 | 257.4744 | -0.00078141 |  | -22.6609 | -1.0537 | 182.231 | -0.00051179 |  | -14.8418 | -0.69014 | 119.3526 | -0.00028311 |  | -8.2101 | -0.38177 | 66.0228 | -8.6703e-05 |  | -2.5144 | -0.11692 | 20.2199 | 8.3807e-05 |  | 2.4304 | 0.11301 | -19.5445 | 0.00023323 |  | 6.7636 | 0.31451 | -54.3907 | 0.00036525 |  | 10.5921 | 0.49253 | -85.1781 | 0.00048273 |  | 13.9992 | 0.65096 | -112.5766 | 0.00058796 |  | 17.0508 | 0.79286 | -137.1168 | 0.00068275 |  | 19.7999 | 0.92069 | -159.2236 | 0.00076859 |  | 22.2892 | 1.0364 | -179.242 | 0.00084669 |  | 24.554 | 1.1418 | -197.4545 | 0.00091804 |  | 26.6233 | 1.238 | -214.0949 | 0.00098349 |  | 28.5213 | 1.3262 | -229.3585 | 0.0010437 |  | 30.2686 | 1.4075 | -243.4092
72 |  | Steel | 72 | 0.0465 |  |  | -41.4589 | -173.2279 |  |  | -0.0019899 |  | -57.708 | -2.6834 | 464.8434 |  | -0.0030997 |  | -60 | -2.79 | 483.3059 |  | -0.004938 |  | -60 | -2.79 | 483.3059 |  | -0.0019899 |  | -57.708 | -2.6834 | 464.8434 |  | -0.0015003 |  | -43.5091 | -2.0232 | 350.4703 | -0.001107 |  | -32.1025 | -1.4928 | 258.5888 | -0.00078408 |  | -22.7382 | -1.0573 | 183.1583 | -0.00051423 |  | -14.9127 | -0.69344 | 120.1235 | -0.00028537 |  | -8.2756 | -0.38482 | 66.6611 | -8.8803e-05 |  | -2.5753 | -0.11975 | 20.7443 | 8.1846e-05 |  | 2.3735 | 0.11037 | -19.119 | 0.00023139 |  | 6.7103 | 0.31203 | -54.0519 | 0.00036351 |  | 10.5419 | 0.4902 | -84.9157 | 0.00048109 |  | 13.9517 | 0.64875 | -112.3824 | 0.00058641 |  | 17.0058 | 0.79077 | -136.9836 | 0.00068128 |  | 19.7571 | 0.91871 | -159.1454 | 0.00076719 |  | 22.2485 | 1.0346 | -179.2136 | 0.00084535 |  | 24.5151 | 1.14 | -197.4714 | 0.00091676 |  | 26.586 | 1.2363 | -214.1532 | 0.00098226 |  | 28.4856 | 1.3246 | -229.4546 | 0.0010426 |  | 30.2343 | 1.4059 | -243.5403
73 |  | Steel | 73 | 0.0465 |  |  | -37.8706 | -173.5173 |  |  | -0.0019936 |  | -57.8136 | -2.6883 | 466.4721 |  | -0.0031042 |  | -60 | -2.79 | 484.1133 |  | -0.0049441 |  | -60 | -2.79 | 484.1133 |  | -0.0019936 |  | -57.8136 | -2.6883 | 466.4721 |  | -0.0015036 |  | -43.6032 | -2.0276 | 351.8151 | -0.0011099 |  | -32.1873 | -1.4967 | 259.7054 | -0.00078674 |  | -22.8154 | -1.0609 | 184.0876 | -0.00051668 |  | -14.9836 | -0.69674 | 120.8963 | -0.00028763 |  | -8.3412 | -0.38786 | 67.3011 | -9.0903e-05 |  | -2.6362 | -0.12258 | 21.2703 | 7.9884e-05 |  | 2.3166 | 0.10772 | -18.6919 | 0.00022955 |  | 6.6569 | 0.30955 | -53.7115 | 0.00036178 |  | 10.4916 | 0.48786 | -84.6521 | 0.00047946 |  | 13.9042 | 0.64655 | -112.187 | 0.00058486 |  | 16.9608 | 0.78868 | -136.8492 | 0.0006798 |  | 19.7143 | 0.91672 | -159.0661 | 0.00076578 |  | 22.2077 | 1.0327 | -179.184 | 0.00084401 |  | 24.4762 | 1.1381 | -197.4872 | 0.00091548 |  | 26.5488 | 1.2345 | -214.2104 | 0.00098103 |  | 28.4499 | 1.3229 | -229.5499 | 0.0010414 |  | 30.2 | 1.4043 | -243.6705
74 |  | Steel | 74 | 0.0465 |  |  | -34.2822 | -173.8067 |  |  | -0.0019972 |  | -57.9192 | -2.6932 | 468.1037 |  | -0.0031087 |  | -60 | -2.79 | 484.9207 |  | -0.0049501 |  | -60 | -2.79 | 484.9207 |  | -0.0019972 |  | -57.9192 | -2.6932 | 468.1037 |  | -0.0015068 |  | -43.6973 | -2.0319 | 353.1624 | -0.0011128 |  | -32.2722 | -1.5007 | 260.8243 | -0.0007894 |  | -22.8927 | -1.0645 | 185.019 | -0.00051912 |  | -15.0546 | -0.70004 | 121.6711 | -0.00028989 |  | -8.4067 | -0.39091 | 67.9429 | -9.3003e-05 |  | -2.6971 | -0.12542 | 21.798 | 7.7923e-05 |  | 2.2598 | 0.10508 | -18.2634 | 0.00022771 |  | 6.6035 | 0.30706 | -53.3698 | 0.00036005 |  | 10.4413 | 0.48552 | -84.387 | 0.00047782 |  | 13.8567 | 0.64434 | -111.9902 | 0.0005833 |  | 16.9158 | 0.78658 | -136.7136 | 0.00067833 |  | 19.6715 | 0.91473 | -158.9856 | 0.00076438 |  | 22.1669 | 1.0308 | -179.1534 | 0.00084266 |  | 24.4372 | 1.1363 | -197.5019 | 0.00091419 |  | 26.5115 | 1.2328 | -214.2666 | 0.0009798 |  | 28.4142 | 1.3213 | -229.6441 | 0.0010402 |  | 30.1657 | 1.4027 | -243.7998
75 |  | Steel | 75 | 0.0465 |  |  | -30.6939 | -174.0961 |  |  | -0.0020009 |  | -58.0248 | -2.6982 | 469.7382 |  | -0.0031133 |  | -60 | -2.79 | 485.7281 |  | -0.0049561 |  | -60 | -2.79 | 485.7281 |  | -0.0020009 |  | -58.0248 | -2.6982 | 469.7382 |  | -0.00151 |  | -43.7914 | -2.0363 | 354.5122 | -0.0011158 |  | -32.3571 | -1.5046 | 261.9455 | -0.00079207 |  | -22.9699 | -1.0681 | 185.9525 | -0.00052157 |  | -15.1255 | -0.70333 | 122.4477 | -0.00029215 |  | -8.4722 | -0.39396 | 68.5865 | -9.5103e-05 |  | -2.758 | -0.12825 | 22.3273 | 7.5961e-05 |  | 2.2029 | 0.10243 | -17.8333 | 0.00022587 |  | 6.5502 | 0.30458 | -53.0266 | 0.00035831 |  | 10.3911 | 0.48319 | -84.1207 | 0.00047618 |  | 13.8092 | 0.64213 | -111.7922 | 0.00058175 |  | 16.8708 | 0.78449 | -136.5768 | 0.00067685 |  | 19.6287 | 0.91274 | -158.9039 | 0.00076297 |  | 22.1262 | 1.0289 | -179.1217 | 0.00084132 |  | 24.3983 | 1.1345 | -197.5156 | 0.00091291 |  | 26.4743 | 1.2311 | -214.3219 | 0.00097857 |  | 28.3785 | 1.3196 | -229.7375 | 0.001039 |  | 30.1314 | 1.4011 | -243.9281
76 |  | Steel | 76 | 0.0465 |  |  | -27.1055 | -174.3855 |  |  | -0.0020045 |  | -58.1305 | -2.7031 | 471.3755 |  | -0.0031178 |  | -60 | -2.79 | 486.5354 |  | -0.0049622 |  | -60 | -2.79 | 486.5354 |  | -0.0020045 |  | -58.1305 | -2.7031 | 471.3755 |  | -0.0015133 |  | -43.8856 | -2.0407 | 355.8646 | -0.0011187 |  | -32.4419 | -1.5085 | 263.069 | -0.00079473 |  | -23.0472 | -1.0717 | 186.888 | -0.00052401 |  | -15.1964 | -0.70663 | 123.2262 | -0.0002944 |  | -8.5377 | -0.397 | 69.2319 | -9.7204e-05 |  | -2.8189 | -0.13108 | 22.8583 | 7.3999e-05 |  | 2.146 | 0.099788 | -17.4016 | 0.00022403 |  | 6.4968 | 0.3021 | -52.682 | 0.00035658 |  | 10.3408 | 0.48085 | -83.8529 | 0.00047454 |  | 13.7617 | 0.63992 | -111.5929 | 0.0005802 |  | 16.8258 | 0.7824 | -136.4388 | 0.00067538 |  | 19.586 | 0.91075 | -158.8211 | 0.00076157 |  | 22.0854 | 1.027 | -179.0889 | 0.00083998 |  | 24.3594 | 1.1327 | -197.5283 | 0.00091162 |  | 26.4371 | 1.2293 | -214.3761 | 0.00097734 |  | 28.3428 | 1.3179 | -229.8298 | 0.0010378 |  | 30.0972 | 1.3995 | -244.0556
77 |  | Steel | 77 | 0.0465 |  |  | -23.5172 | -174.6748 |  |  | -0.0020081 |  | -58.2361 | -2.708 | 473.0156 |  | -0.0031224 |  | -60 | -2.79 | 487.3428 |  | -0.0049682 |  | -60 | -2.79 | 487.3428 |  | -0.0020081 |  | -58.2361 | -2.708 | 473.0156 |  | -0.0015165 |  | -43.9797 | -2.0451 | 357.2195 | -0.0011216 |  | -32.5268 | -1.5125 | 264.1947 | -0.0007974 |  | -23.1245 | -1.0753 | 187.8257 | -0.00052646 |  | -15.2673 | -0.70993 | 124.0066 | -0.00029666 |  | -8.6033 | -0.40005 | 69.879 | -9.9304e-05 |  | -2.8798 | -0.13391 | 23.3909 | 7.2038e-05 |  | 2.0891 | 0.097143 | -16.9684 | 0.00022219 |  | 6.4434 | 0.29962 | -52.3359 | 0.00035485 |  | 10.2906 | 0.47851 | -83.5838 | 0.0004729 |  | 13.7142 | 0.63771 | -111.3923 | 0.00057865 |  | 16.7807 | 0.7803 | -136.2996 | 0.0006739 |  | 19.5432 | 0.90876 | -158.7371 | 0.00076016 |  | 22.0446 | 1.0251 | -179.055 | 0.00083864 |  | 24.3204 | 1.1309 | -197.5399 | 0.00091034 |  | 26.3998 | 1.2276 | -214.4293 | 0.00097611 |  | 28.3071 | 1.3163 | -229.9212 | 0.0010367 |  | 30.0629 | 1.3979 | -244.1821
78 |  | Steel | 78 | 0.0465 |  |  | -19.9288 | -174.9642 |  |  | -0.0020118 |  | -58.3417 | -2.7129 | 474.6586 |  | -0.0031269 |  | -60 | -2.79 | 488.1502 |  | -0.0049742 |  | -60 | -2.79 | 488.1502 |  | -0.0020118 |  | -58.3417 | -2.7129 | 474.6586 |  | -0.0015198 |  | -44.0738 | -2.0494 | 358.5769 | -0.0011245 |  | -32.6116 | -1.5164 | 265.3228 | -0.00080006 |  | -23.2017 | -1.0789 | 188.7654 | -0.0005289 |  | -15.3382 | -0.71323 | 124.789 | -0.00029892 |  | -8.6688 | -0.4031 | 70.5278 | -0.0001014 |  | -2.9407 | -0.13674 | 23.9251 | 7.0076e-05 |  | 2.0322 | 0.094498 | -16.5337 | 0.00022035 |  | 6.3901 | 0.29714 | -51.9884 | 0.00035311 |  | 10.2403 | 0.47617 | -83.3134 | 0.00047127 |  | 13.6667 | 0.6355 | -111.1904 | 0.00057709 |  | 16.7357 | 0.77821 | -136.1591 | 0.00067243 |  | 19.5004 | 0.90677 | -158.652 | 0.00075875 |  | 22.0039 | 1.0232 | -179.02 | 0.00083729 |  | 24.2815 | 1.1291 | -197.5505 | 0.00090905 |  | 26.3626 | 1.2259 | -214.4815 | 0.00097488 |  | 28.2714 | 1.3146 | -230.0116 | 0.0010355 |  | 30.0286 | 1.3963 | -244.3077
79 |  | Steel | 79 | 0.0465 |  |  | 35.2919 | -179.4175 |  |  | -0.0020678 |  | -59.9672 | -2.7885 | 500.3008 |  | -0.0031968 |  | -60 | -2.79 | 500.5749 |  | -0.0050671 |  | -60 | -2.79 | 500.5749 |  | -0.0020678 |  | -59.9672 | -2.7885 | 500.3008 |  | -0.0015697 |  | -45.522 | -2.1168 | 379.7858 | -0.0011696 |  | -33.9174 | -1.5772 | 282.9701 | -0.00084106 |  | -24.3906 | -1.1342 | 203.4888 | -0.00056653 |  | -16.4294 | -0.76397 | 137.0691 | -0.00033369 |  | -9.6771 | -0.44999 | 80.7356 | -0.00013372 |  | -3.8779 | -0.18032 | 32.353 | 3.9889e-05 |  | 1.1568 | 0.053791 | -9.651 | 0.00019203 |  | 5.5688 | 0.25895 | -46.4598 | 0.00032644 |  | 9.4668 | 0.44021 | -78.9811 | 0.00044606 |  | 12.9359 | 0.60152 | -107.9228 | 0.00055321 |  | 16.043 | 0.746 | -133.8451 | 0.00064972 |  | 18.842 | 0.87615 | -157.197 | 0.00073712 |  | 21.3766 | 0.99401 | -178.3429 | 0.00081664 |  | 23.6825 | 1.1012 | -197.5811 | 0.00088929 |  | 25.7894 | 1.1992 | -215.1588 | 0.00095593 |  | 27.722 | 1.2891 | -231.282 | 0.0010173 |  | 29.501 | 1.3718 | -246.124
80 |  | Steel | 80 | 0.0465 |  |  | 30.5074 | -179.0317 |  |  | -0.002063 |  | -59.8263 | -2.7819 | 498.0525 |  | -0.0031908 |  | -60 | -2.79 | 499.4984 |  | -0.005059 |  | -60 | -2.79 | 499.4984 |  | -0.002063 |  | -59.8263 | -2.7819 | 498.0525 |  | -0.0015654 |  | -45.3965 | -2.1109 | 377.9245 | -0.0011657 |  | -33.8043 | -1.5719 | 281.4197 | -0.0008375 |  | -24.2876 | -1.1294 | 202.1937 | -0.00056327 |  | -16.3349 | -0.75957 | 135.9872 | -0.00033068 |  | -9.5898 | -0.44592 | 79.8346 | -0.00013092 |  | -3.7967 | -0.17655 | 31.6074 | 4.2505e-05 |  | 1.2326 | 0.057318 | -10.2617 | 0.00019448 |  | 5.6399 | 0.26226 | -46.9523 | 0.00032875 |  | 9.5339 | 0.44332 | -79.3691 | 0.00044825 |  | 12.9992 | 0.60446 | -108.2179 | 0.00055528 |  | 16.103 | 0.74879 | -134.0569 | 0.00065169 |  | 18.899 | 0.8788 | -157.3339 | 0.000739 |  | 21.4309 | 0.99654 | -178.4118 | 0.00081843 |  | 23.7344 | 1.1036 | -197.5883 | 0.000891 |  | 25.8391 | 1.2015 | -215.1095 | 0.00095757 |  | 27.7696 | 1.2913 | -231.1809 | 0.0010189 |  | 29.5467 | 1.3739 | -245.9753
81 |  | Steel | 81 | 0.0465 |  |  | 25.7229 | -178.6458 |  |  | -0.0020581 |  | -59.6855 | -2.7754 | 495.8092 |  | -0.0031847 |  | -60 | -2.79 | 498.4218 |  | -0.005051 |  | -60 | -2.79 | 498.4218 |  | -0.0020581 |  | -59.6855 | -2.7754 | 495.8092 |  | -0.0015611 |  | -45.271 | -2.1051 | 376.0676 | -0.0011618 |  | -33.6911 | -1.5666 | 279.8733 | -0.00083395 |  | -24.1846 | -1.1246 | 200.9022 | -0.00056001 |  | -16.2403 | -0.75517 | 134.9087 | -0.00032767 |  | -9.5024 | -0.44186 | 78.9368 | -0.00012812 |  | -3.7155 | -0.17277 | 30.8648 | 4.512e-05 |  | 1.3085 | 0.060845 | -10.8696 | 0.00019693 |  | 5.7111 | 0.26557 | -47.4422 | 0.00033106 |  | 9.6009 | 0.44644 | -79.7548 | 0.00045043 |  | 13.0625 | 0.60741 | -108.5107 | 0.00055735 |  | 16.163 | 0.75158 | -134.2666 | 0.00065366 |  | 18.9561 | 0.88146 | -157.4687 | 0.00074087 |  | 21.4853 | 0.99907 | -178.4788 | 0.00082022 |  | 23.7863 | 1.1061 | -197.5936 | 0.00089271 |  | 25.8887 | 1.2038 | -215.0584 | 0.00095921 |  | 27.8172 | 1.2935 | -231.0781 | 0.0010204 |  | 29.5924 | 1.376 | -245.8249
82 |  | Steel | 82 | 0.0465 |  |  | 20.9385 | -178.26 |  |  | -0.0020533 |  | -59.5447 | -2.7688 | 493.571 |  | -0.0031786 |  | -60 | -2.79 | 497.3453 |  | -0.005043 |  | -60 | -2.79 | 497.3453 |  | -0.0020533 |  | -59.5447 | -2.7688 | 493.571 |  | -0.0015567 |  | -45.1455 | -2.0993 | 374.2153 | -0.0011579 |  | -33.578 | -1.5614 | 278.331 | -0.0008304 |  | -24.0816 | -1.1198 | 199.6144 | -0.00055675 |  | -16.1458 | -0.75078 | 133.8337 | -0.00032466 |  | -9.415 | -0.4378 | 78.0421 | -0.00012532 |  | -3.6343 | -0.16899 | 30.125 | 4.7736e-05 |  | 1.3843 | 0.064372 | -11.4749 | 0.00019939 |  | 5.7822 | 0.26887 | -47.9296 | 0.00033338 |  | 9.6679 | 0.44956 | -80.138 | 0.00045262 |  | 13.1258 | 0.61035 | -108.8013 | 0.00055941 |  | 16.223 | 0.75437 | -134.4742 | 0.00065562 |  | 19.0131 | 0.88411 | -157.6015 | 0.00074275 |  | 21.5396 | 1.0016 | -178.5439 | 0.00082201 |  | 23.8382 | 1.1085 | -197.597 | 0.00089443 |  | 25.9384 | 1.2061 | -215.0056 | 0.00096085 |  | 27.8648 | 1.2957 | -230.9737 | 0.001022 |  | 29.6381 | 1.3782 | -245.6729
83 |  | Steel | 83 | 0.0465 |  |  | 16.154 | -177.8741 |  |  | -0.0020484 |  | -59.4038 | -2.7623 | 491.3378 |  | -0.0031726 |  | -60 | -2.79 | 496.2688 |  | -0.0050349 |  | -60 | -2.79 | 496.2688 |  | -0.0020484 |  | -59.4038 | -2.7623 | 491.3378 |  | -0.0015524 |  | -45.0201 | -2.0934 | 372.3675 | -0.001154 |  | -33.4649 | -1.5561 | 276.7928 | -0.00082685 |  | -23.9786 | -1.115 | 198.3304 | -0.00055349 |  | -16.0512 | -0.74638 | 132.762 | -0.00032164 |  | -9.3277 | -0.43374 | 77.1506 | -0.00012252 |  | -3.5531 | -0.16522 | 29.3882 | 5.0351e-05 |  | 1.4602 | 0.067899 | -12.0774 | 0.00020184 |  | 5.8534 | 0.27218 | -48.4144 | 0.00033569 |  | 9.7349 | 0.45267 | -80.5188 | 0.0004548 |  | 13.1892 | 0.6133 | -109.0896 | 0.00056148 |  | 16.2831 | 0.75716 | -134.6796 | 0.00065759 |  | 19.0702 | 0.88676 | -157.7322 | 0.00074462 |  | 21.594 | 1.0041 | -178.607 | 0.0008238 |  | 23.8901 | 1.1109 | -197.5986 | 0.00089614 |  | 25.988 | 1.2084 | -214.951 | 0.0009625 |  | 27.9124 | 1.2979 | -230.8675 | 0.0010236 |  | 29.6838 | 1.3803 | -245.5193
84 |  | Steel | 84 | 0.0465 |  |  | 11.3695 | -177.4883 |  |  | -0.0020436 |  | -59.263 | -2.7557 | 489.1096 |  | -0.0031665 |  | -60 | -2.79 | 495.1923 |  | -0.0050269 |  | -60 | -2.79 | 495.1923 |  | -0.0020436 |  | -59.263 | -2.7557 | 489.1096 |  | -0.0015481 |  | -44.8946 | -2.0876 | 370.5242 | -0.0011501 |  | -33.3517 | -1.5509 | 275.2586 | -0.0008233 |  | -23.8756 | -1.1102 | 197.05 | -0.00055023 |  | -15.9567 | -0.74199 | 131.6937 | -0.00031863 |  | -9.2403 | -0.42967 | 76.2622 | -0.00011972 |  | -3.4719 | -0.16144 | 28.6543 | 5.2967e-05 |  | 1.536 | 0.071426 | -12.6772 | 0.0002043 |  | 5.9246 | 0.27549 | -48.8966 | 0.000338 |  | 9.8019 | 0.45579 | -80.8972 | 0.00045698 |  | 13.2525 | 0.61624 | -109.3756 | 0.00056355 |  | 16.3431 | 0.75995 | -134.8828 | 0.00065956 |  | 19.1272 | 0.88942 | -157.8608 | 0.00074649 |  | 21.6483 | 1.0066 | -178.6681 | 0.00082559 |  | 23.942 | 1.1133 | -197.5983 | 0.00089785 |  | 26.0377 | 1.2108 | -214.8945 | 0.00096414 |  | 27.96 | 1.3001 | -230.7596 | 0.0010252 |  | 29.7295 | 1.3824 | -245.364
85 |  | Steel | 85 | 0.0465 |  |  | 6.5851 | -177.1024 |  |  | -0.0020387 |  | -59.1222 | -2.7492 | 486.8866 |  | -0.0031605 |  | -60 | -2.79 | 494.1158 |  | -0.0050188 |  | -60 | -2.79 | 494.1158 |  | -0.0020387 |  | -59.1222 | -2.7492 | 486.8866 |  | -0.0015438 |  | -44.7691 | -2.0818 | 368.6854 | -0.0011462 |  | -33.2386 | -1.5456 | 273.7285 | -0.00081974 |  | -23.7726 | -1.1054 | 195.7733 | -0.00054697 |  | -15.8621 | -0.73759 | 130.6288 | -0.00031562 |  | -9.1529 | -0.42561 | 75.3769 | -0.00011692 |  | -3.3907 | -0.15767 | 27.9233 | 5.5582e-05 |  | 1.6119 | 0.074952 | -13.2743 | 0.00020675 |  | 5.9957 | 0.2788 | -49.3763 | 0.00034031 |  | 9.8689 | 0.45891 | -81.2733 | 0.00045917 |  | 13.3158 | 0.61919 | -109.6593 | 0.00056562 |  | 16.4031 | 0.76274 | -135.0839 | 0.00066153 |  | 19.1843 | 0.89207 | -157.9874 | 0.00074837 |  | 21.7027 | 1.0092 | -178.7273 | 0.00082738 |  | 23.9939 | 1.1157 | -197.5962 | 0.00089956 |  | 26.0874 | 1.2131 | -214.8363 | 0.00096578 |  | 28.0076 | 1.3024 | -230.65 | 0.0010267 |  | 29.7753 | 1.3845 | -245.2071
86 |  | Steel | 86 | 0.0465 |  |  | 1.8006 | -176.7166 |  |  | -0.0020338 |  | -58.9813 | -2.7426 | 484.6686 |  | -0.0031544 |  | -60 | -2.79 | 493.0393 |  | -0.0050108 |  | -60 | -2.79 | 493.0393 |  | -0.0020338 |  | -58.9813 | -2.7426 | 484.6686 |  | -0.0015394 |  | -44.6436 | -2.0759 | 366.8511 | -0.0011423 |  | -33.1255 | -1.5403 | 272.2025 | -0.00081619 |  | -23.6696 | -1.1006 | 194.5003 | -0.00054371 |  | -15.7676 | -0.73319 | 129.5673 | -0.00031261 |  | -9.0656 | -0.42155 | 74.4948 | -0.00011412 |  | -3.3095 | -0.15389 | 27.1952 | 5.8198e-05 |  | 1.6877 | 0.078479 | -13.8686 | 0.0002092 |  | 6.0669 | 0.28211 | -49.8535 | 0.00034262 |  | 9.9359 | 0.46202 | -81.6469 | 0.00046135 |  | 13.3791 | 0.62213 | -109.9407 | 0.00056769 |  | 16.4631 | 0.76554 | -135.2828 | 0.00066349 |  | 19.2413 | 0.89472 | -158.112 | 0.00075024 |  | 21.757 | 1.0117 | -178.7845 | 0.00082917 |  | 24.0458 | 1.1181 | -197.5922 | 0.00090128 |  | 26.137 | 1.2154 | -214.7764 | 0.00096742 |  | 28.0552 | 1.3046 | -230.5387 | 0.0010283 |  | 29.821 | 1.3867 | -245.0485
87 |  | Steel | 87 | 0.0465 |  |  | -2.9839 | -176.3308 |  |  | -0.002029 |  | -58.8405 | -2.7361 | 482.4556 |  | -0.0031484 |  | -60 | -2.79 | 491.9628 |  | -0.0050027 |  | -60 | -2.79 | 491.9628 |  | -0.002029 |  | -58.8405 | -2.7361 | 482.4556 |  | -0.0015351 |  | -44.5182 | -2.0701 | 365.0213 | -0.0011384 |  | -33.0123 | -1.5351 | 270.6805 | -0.00081264 |  | -23.5665 | -1.0958 | 193.231 | -0.00054045 |  | -15.673 | -0.7288 | 128.5092 | -0.00030959 |  | -8.9782 | -0.41749 | 73.6158 | -0.00011132 |  | -3.2283 | -0.15012 | 26.47 | 6.0813e-05 |  | 1.7636 | 0.082006 | -14.4603 | 0.00021166 |  | 6.138 | 0.28542 | -50.3281 | 0.00034493 |  | 10.003 | 0.46514 | -82.0181 | 0.00046353 |  | 13.4425 | 0.62507 | -110.2199 | 0.00056976 |  | 16.5231 | 0.76833 | -135.4796 | 0.00066546 |  | 19.2984 | 0.89737 | -158.2345 | 0.00075212 |  | 21.8114 | 1.0142 | -178.8398 | 0.00083096 |  | 24.0977 | 1.1205 | -197.5863 | 0.00090299 |  | 26.1867 | 1.2177 | -214.7146 | 0.00096906 |  | 28.1028 | 1.3068 | -230.4256 | 0.0010299 |  | 29.8667 | 1.3888 | -244.8883
88 |  | Steel | 88 | 0.0465 |  |  | -7.7683 | -175.9449 |  |  | -0.0020241 |  | -58.6997 | -2.7295 | 480.2477 |  | -0.0031423 |  | -60 | -2.79 | 490.8863 |  | -0.0049947 |  | -60 | -2.79 | 490.8863 |  | -0.0020241 |  | -58.6997 | -2.7295 | 480.2477 |  | -0.0015308 |  | -44.3927 | -2.0643 | 363.196 | -0.0011345 |  | -32.8992 | -1.5298 | 269.1626 | -0.00080909 |  | -23.4635 | -1.0911 | 191.9655 | -0.00053719 |  | -15.5785 | -0.7244 | 127.4545 | -0.00030658 |  | -8.8908 | -0.41342 | 72.7399 | -0.00010852 |  | -3.1471 | -0.14634 | 25.7477 | 6.3429e-05 |  | 1.8394 | 0.085533 | -15.0492 | 0.00021411 |  | 6.2092 | 0.28873 | -50.8002 | 0.00034724 |  | 10.07 | 0.46825 | -82.3869 | 0.00046572 |  | 13.5058 | 0.62802 | -110.4968 | 0.00057183 |  | 16.5832 | 0.77112 | -135.6742 | 0.00066743 |  | 19.3554 | 0.90003 | -158.355 | 0.00075399 |  | 21.8657 | 1.0168 | -178.8932 | 0.00083275 |  | 24.1496 | 1.123 | -197.5786 | 0.0009047 |  | 26.2363 | 1.22 | -214.6511 | 0.0009707 |  | 28.1504 | 1.309 | -230.3109 | 0.0010315 |  | 29.9124 | 1.3909 | -244.7264
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33 |  | Concrete | 1 | 55.8 |  |  | -35.4526 | 177.424 |  |  | 0.0024234 | 1.9538 |  | 109.0225 | 19343.2094 |  | 0.0024045 | 1.982 |  | 110.5975 | 19622.6538 |  | 0.0023732 | 2.0273 |  | 113.1226 | 20070.6712 |  | 0.0024234 | 1.9538 |  | 109.0225 | 19343.2094 |  | 0.0024318 | 1.9411 |  | 108.3155 | 19217.7632 | 0.0024385 | 1.9309 |  | 107.7421 | 19116.0306 | 0.002444 | 1.9224 |  | 107.2678 | 19031.8765 | 0.0024486 | 1.9152 |  | 106.8689 | 18961.1117 | 0.0024525 | 1.9091 |  | 106.5289 | 18900.779 | 0.0024559 | 1.9039 |  | 106.2355 | 18848.7315 | 0.0024588 | 1.8993 |  | 105.9799 | 18803.3734 | 0.0024613 | 1.8953 |  | 105.7551 | 18763.4936 | 0.0024636 | 1.8917 |  | 105.5559 | 18728.1567 | 0.0024656 | 1.8885 |  | 105.3782 | 18696.6284 | 0.0024674 | 1.8856 |  | 105.2187 | 18668.3249 | 0.002469 | 1.8831 |  | 105.0747 | 18642.7755 | 0.0024704 | 1.8807 |  | 104.9441 | 18619.5972 | 0.0024718 | 1.8786 |  | 104.825 | 18598.4744 | 0.002473 | 1.8766 |  | 104.7161 | 18579.1456 | 0.0024741 | 1.8748 |  | 104.616 | 18561.3914 | 0.0024751 | 1.8732 |  | 104.5238 | 18545.0272
34 |  | Concrete | 2 | 55.8 |  |  | -30.6682 | 177.0381 |  |  | 0.0024186 | 1.9611 |  | 109.4303 | 19373.3421 |  | 0.0023985 | 1.9909 |  | 111.0935 | 19667.7906 |  | 0.0023651 | 2.0386 |  | 113.7537 | 20138.7492 |  | 0.0024186 | 1.9611 |  | 109.4303 | 19373.3421 |  | 0.0024275 | 1.9477 |  | 108.6828 | 19240.9994 | 0.0024346 | 1.9368 |  | 108.0762 | 19133.6037 | 0.0024404 | 1.9279 |  | 107.5741 | 19044.7188 | 0.0024453 | 1.9203 |  | 107.1517 | 18969.9441 | 0.0024495 | 1.9138 |  | 106.7915 | 18906.1701 | 0.0024531 | 1.9083 |  | 106.4807 | 18851.1376 | 0.0024561 | 1.9034 |  | 106.2097 | 18803.1657 | 0.0024589 | 1.8991 |  | 105.9714 | 18760.9786 | 0.0024613 | 1.8953 |  | 105.7602 | 18723.5899 | 0.0024634 | 1.892 |  | 105.5717 | 18690.2254 | 0.0024653 | 1.8889 |  | 105.4025 | 18660.2688 | 0.002467 | 1.8862 |  | 105.2498 | 18633.2237 | 0.0024686 | 1.8837 |  | 105.1112 | 18608.6853 | 0.00247 | 1.8814 |  | 104.9848 | 18586.3208 | 0.0024713 | 1.8794 |  | 104.8692 | 18565.8535 | 0.0024725 | 1.8775 |  | 104.763 | 18547.052 | 0.0024736 | 1.8757 |  | 104.6651 | 18529.7209
35 |  | Concrete | 3 | 55.8 |  |  | -25.8837 | 176.6523 |  |  | 0.0024137 | 1.9684 |  | 109.8356 | 19402.7158 |  | 0.0023924 | 1.9997 |  | 111.5856 | 19711.8537 |  | 0.0023571 | 2.0498 |  | 114.3779 | 20205.121 |  | 0.0024137 | 1.9684 |  | 109.8356 | 19402.7158 |  | 0.0024231 | 1.9543 |  | 109.0481 | 19263.5994 | 0.0024307 | 1.9428 |  | 108.4086 | 19150.6323 | 0.0024369 | 1.9333 |  | 107.8791 | 19057.087 | 0.0024421 | 1.9253 |  | 107.4334 | 18978.3581 | 0.0024465 | 1.9185 |  | 107.0532 | 18911.1876 | 0.0024503 | 1.9126 |  | 106.7249 | 18853.2067 | 0.0024535 | 1.9075 |  | 106.4388 | 18802.6519 | 0.0024564 | 1.903 |  | 106.187 | 18758.1832 | 0.0024589 | 1.899 |  | 105.9639 | 18718.7649 | 0.0024612 | 1.8954 |  | 105.7647 | 18683.5832 | 0.0024632 | 1.8922 |  | 105.5859 | 18651.9902 | 0.0024651 | 1.8893 |  | 105.4244 | 18623.4638 | 0.0024667 | 1.8867 |  | 105.2779 | 18597.5784 | 0.0024682 | 1.8843 |  | 105.1443 | 18573.9834 | 0.0024696 | 1.8821 |  | 105.0221 | 18552.388 | 0.0024708 | 1.8801 |  | 104.9098 | 18532.5483 | 0.002472 | 1.8782 |  | 104.8062 | 18514.2587
36 |  | Concrete | 4 | 55.8 |  |  | -21.0992 | 176.2665 |  |  | 0.0024089 | 1.9756 |  | 110.2384 | 19431.3334 |  | 0.0023863 | 2.0085 |  | 112.0738 | 19754.8474 |  | 0.002349 | 2.0608 |  | 114.9952 | 20269.7944 |  | 0.0024089 | 1.9756 |  | 110.2384 | 19431.3334 |  | 0.0024188 | 1.9608 |  | 109.4114 | 19285.5655 | 0.0024268 | 1.9487 |  | 108.7395 | 19167.1182 | 0.0024333 | 1.9388 |  | 108.1827 | 19068.9827 | 0.0024388 | 1.9304 |  | 107.7139 | 18986.3548 | 0.0024435 | 1.9232 |  | 107.3139 | 18915.8326 | 0.0024475 | 1.917 |  | 106.9684 | 18854.94 | 0.0024509 | 1.9116 |  | 106.6671 | 18801.8326 | 0.002454 | 1.9068 |  | 106.402 | 18755.1083 | 0.0024566 | 1.9026 |  | 106.167 | 18713.6823 | 0.002459 | 1.8989 |  | 105.9572 | 18676.7024 | 0.0024612 | 1.8955 |  | 105.7688 | 18643.4896 | 0.0024631 | 1.8924 |  | 105.5986 | 18613.4965 | 0.0024648 | 1.8897 |  | 105.4442 | 18586.2767 | 0.0024664 | 1.8872 |  | 105.3034 | 18561.4628 | 0.0024679 | 1.8848 |  | 105.1746 | 18538.7495 | 0.0024692 | 1.8827 |  | 105.0562 | 18517.8808 | 0.0024704 | 1.8808 |  | 104.947 | 18498.6409
37 |  | Concrete | 5 | 55.8 |  |  | -16.3148 | 175.8806 |  |  | 0.002404 | 1.9828 |  | 110.6387 | 19459.1978 |  | 0.0023803 | 2.0172 |  | 112.558 | 19796.7764 |  | 0.002341 | 2.0718 |  | 115.6056 | 20332.7776 |  | 0.002404 | 1.9828 |  | 110.6387 | 19459.1978 |  | 0.0024145 | 1.9673 |  | 109.7728 | 19306.9002 | 0.0024229 | 1.9546 |  | 109.0687 | 19183.0633 | 0.0024298 | 1.9442 |  | 108.485 | 19080.4074 | 0.0024356 | 1.9354 |  | 107.9933 | 18993.9358 | 0.0024404 | 1.9278 |  | 107.5736 | 18920.1061 | 0.0024447 | 1.9213 |  | 107.211 | 18856.3383 | 0.0024483 | 1.9157 |  | 106.8947 | 18800.7088 | 0.0024515 | 1.9107 |  | 106.6164 | 18751.7545 | 0.0024543 | 1.9063 |  | 106.3696 | 18708.3429 | 0.0024568 | 1.9023 |  | 106.1492 | 18669.5836 | 0.0024591 | 1.8988 |  | 105.9512 | 18634.7675 | 0.0024611 | 1.8956 |  | 105.7724 | 18603.3221 | 0.002463 | 1.8927 |  | 105.6102 | 18574.7809 | 0.0024646 | 1.89 |  | 105.4622 | 18548.7594 | 0.0024662 | 1.8876 |  | 105.3268 | 18524.9382 | 0.0024676 | 1.8853 |  | 105.2023 | 18503.0497 | 0.0024688 | 1.8833 |  | 105.0876 | 18482.8679
38 |  | Concrete | 6 | 55.8 |  |  | -11.5303 | 175.4948 |  |  | 0.0023992 | 1.9899 |  | 111.0364 | 19486.312 |  | 0.0023742 | 2.0258 |  | 113.0384 | 19837.6452 |  | 0.0023329 | 2.0826 |  | 116.209 | 20394.0785 |  | 0.0023992 | 1.9899 |  | 111.0364 | 19486.312 |  | 0.0024101 | 1.9737 |  | 110.1321 | 19327.6057 | 0.002419 | 1.9605 |  | 109.3963 | 19198.4695 | 0.0024262 | 1.9496 |  | 108.7859 | 19091.3628 | 0.0024323 | 1.9404 |  | 108.2716 | 19001.1022 | 0.0024374 | 1.9325 |  | 107.8323 | 18924.0094 | 0.0024419 | 1.9257 |  | 107.4528 | 18857.4027 | 0.0024457 | 1.9197 |  | 107.1216 | 18799.2814 | 0.002449 | 1.9145 |  | 106.8301 | 18748.1226 | 0.002452 | 1.9099 |  | 106.5715 | 18702.7471 | 0.0024547 | 1.9057 |  | 106.3407 | 18662.2275 | 0.002457 | 1.902 |  | 106.1332 | 18625.8244 | 0.0024591 | 1.8987 |  | 105.9458 | 18592.9412 | 0.0024611 | 1.8956 |  | 105.7758 | 18563.0912 | 0.0024628 | 1.8928 |  | 105.6207 | 18535.8734 | 0.0024644 | 1.8903 |  | 105.4787 | 18510.9546 | 0.0024659 | 1.888 |  | 105.3482 | 18488.0554 | 0.0024673 | 1.8858 |  | 105.2279 | 18466.9399
39 |  | Concrete | 7 | 55.8 |  |  | -6.7458 | 175.1089 |  |  | 0.0023943 | 1.997 |  | 111.4317 | 19512.6788 |  | 0.0023682 | 2.0343 |  | 113.5148 | 19877.4583 |  | 0.0023249 | 2.0933 |  | 116.8056 | 20453.705 |  | 0.0023943 | 1.997 |  | 111.4317 | 19512.6788 |  | 0.0024058 | 1.9801 |  | 110.4894 | 19347.6843 | 0.0024151 | 1.9663 |  | 109.7222 | 19213.3387 | 0.0024227 | 1.9549 |  | 109.0855 | 19101.8503 | 0.002429 | 1.9453 |  | 108.5488 | 19007.8554 | 0.0024344 | 1.9371 |  | 108.0901 | 18927.5435 | 0.0024391 | 1.93 |  | 107.6937 | 18858.1341 | 0.0024431 | 1.9238 |  | 107.3478 | 18797.5511 | 0.0024466 | 1.9183 |  | 107.0432 | 18744.2134 | 0.0024497 | 1.9135 |  | 106.7729 | 18696.8959 | 0.0024525 | 1.9092 |  | 106.5316 | 18654.6346 | 0.0024549 | 1.9053 |  | 106.3147 | 18616.6609 | 0.0024572 | 1.9018 |  | 106.1188 | 18582.3542 | 0.0024592 | 1.8986 |  | 105.941 | 18551.2081 | 0.002461 | 1.8957 |  | 105.7788 | 18522.8054 | 0.0024627 | 1.893 |  | 105.6303 | 18496.7991 | 0.0024643 | 1.8906 |  | 105.4938 | 18472.8982 | 0.0024657 | 1.8883 |  | 105.3679 | 18450.8572
40 |  | Concrete | 8 | 55.8 |  |  | -1.9614 | 174.7231 |  |  | 0.0023894 | 2.004 |  | 111.8244 | 19538.3012 |  | 0.0023621 | 2.0428 |  | 113.9873 | 19916.2203 |  | 0.0023168 | 2.1039 |  | 117.3953 | 20511.6652 |  | 0.0023894 | 2.004 |  | 111.8244 | 19538.3012 |  | 0.0024015 | 1.9865 |  | 110.8448 | 19367.1383 | 0.0024112 | 1.9722 |  | 110.0466 | 19227.6728 | 0.0024191 | 1.9603 |  | 109.3838 | 19111.8715 | 0.0024258 | 1.9503 |  | 108.8248 | 19014.1966 | 0.0024314 | 1.9417 |  | 108.3469 | 18930.7096 | 0.0024363 | 1.9343 |  | 107.9338 | 18858.5335 | 0.0024405 | 1.9278 |  | 107.5732 | 18795.5188 | 0.0024441 | 1.9221 |  | 107.2556 | 18740.0275 | 0.0024474 | 1.9171 |  | 106.9738 | 18690.7896 | 0.0024503 | 1.9126 |  | 106.7221 | 18646.8055 | 0.0024529 | 1.9085 |  | 106.4958 | 18607.2775 | 0.0024552 | 1.9049 |  | 106.2914 | 18571.5616 | 0.0024573 | 1.9015 |  | 106.1058 | 18539.1321 | 0.0024593 | 1.8985 |  | 105.9365 | 18509.5557 | 0.002461 | 1.8957 |  | 105.7815 | 18482.4719 | 0.0024626 | 1.8932 |  | 105.639 | 18457.5785 | 0.0024641 | 1.8908 |  | 105.5076 | 18434.6202
41 |  | Concrete | 9 | 55.8 |  |  | 2.8231 | 174.3372 |  |  | 0.0023846 | 2.011 |  | 112.2146 | 19563.182 |  | 0.0023561 | 2.0512 |  | 114.456 | 19953.9356 |  | 0.0023088 | 2.1143 |  | 117.9781 | 20567.9671 |  | 0.0023846 | 2.011 |  | 112.2146 | 19563.182 |  | 0.0023972 | 1.9928 |  | 111.1981 | 19385.9701 | 0.0024073 | 1.9779 |  | 110.3693 | 19241.4736 | 0.0024156 | 1.9656 |  | 109.6807 | 19121.4279 | 0.0024225 | 1.9552 |  | 109.0996 | 19020.1273 | 0.0024284 | 1.9463 |  | 108.6028 | 18933.5087 | 0.0024335 | 1.9386 |  | 108.1731 | 18858.6018 | 0.0024378 | 1.9319 |  | 107.7979 | 18793.1854 | 0.0024417 | 1.9259 |  | 107.4674 | 18735.5658 | 0.0024451 | 1.9207 |  | 107.1741 | 18684.4292 | 0.0024481 | 1.916 |  | 106.912 | 18638.7407 | 0.0024508 | 1.9118 |  | 106.6764 | 18597.6747 | 0.0024532 | 1.9079 |  | 106.4636 | 18560.5639 | 0.0024555 | 1.9045 |  | 106.2703 | 18526.8636 | 0.0024575 | 1.9013 |  | 106.0939 | 18496.1247 | 0.0024593 | 1.8984 |  | 105.9325 | 18467.9735 | 0.002461 | 1.8958 |  | 105.784 | 18442.0965 | 0.0024625 | 1.8933 |  | 105.6471 | 18418.2292
42 |  | Concrete | 10 | 55.8 |  |  | 7.6076 | 173.9514 |  |  | 0.0023797 | 2.018 |  | 112.6023 | 19587.3243 |  | 0.00235 | 2.0595 |  | 114.9207 | 19990.6088 |  | 0.0023008 | 2.1246 |  | 118.5539 | 20622.6186 |  | 0.0023797 | 2.018 |  | 112.6023 | 19587.3243 |  | 0.0023928 | 1.9991 |  | 111.5495 | 19404.1819 | 0.0024034 | 1.9837 |  | 110.6904 | 19254.743 | 0.002412 | 1.9709 |  | 109.9763 | 19130.5212 | 0.0024193 | 1.9601 |  | 109.3734 | 19025.6487 | 0.0024254 | 1.9509 |  | 108.8577 | 18935.9421 | 0.0024307 | 1.9429 |  | 108.4116 | 18858.3401 | 0.0024352 | 1.9359 |  | 108.0219 | 18790.5517 | 0.0024392 | 1.9297 |  | 107.6785 | 18730.829 | 0.0024428 | 1.9243 |  | 107.3738 | 18677.8151 | 0.0024459 | 1.9194 |  | 107.1014 | 18630.4409 | 0.0024487 | 1.915 |  | 106.8566 | 18587.853 | 0.0024513 | 1.911 |  | 106.6353 | 18549.3615 | 0.0024536 | 1.9074 |  | 106.4344 | 18514.403 | 0.0024557 | 1.9041 |  | 106.251 | 18482.5128 | 0.0024576 | 1.9011 |  | 106.0831 | 18453.3041 | 0.0024593 | 1.8984 |  | 105.9287 | 18426.4527 | 0.002461 | 1.8958 |  | 105.7864 | 18401.6844
43 |  | Concrete | 11 | 27.9 |  |  | 40.7001 | 171.2826 |  |  | 0.0023461 | 2.0648 |  | 57.6075 | 9867.1615 |  | 0.0023081 | 2.1152 |  | 59.0139 | 10108.0512 |  | 0.0022451 | 2.1926 |  | 61.174 | 10478.0455 |  | 0.0023461 | 2.0648 |  | 57.6075 | 9867.1615 |  | 0.0023629 | 2.0417 |  | 56.9625 | 9756.6808 | 0.0023764 | 2.0227 |  | 56.4334 | 9666.0638 | 0.0023875 | 2.0069 |  | 55.9918 | 9590.4311 | 0.0023967 | 1.9935 |  | 55.6178 | 9526.3697 | 0.0024045 | 1.982 |  | 55.2971 | 9471.4244 | 0.0024113 | 1.972 |  | 55.0189 | 9423.7855 | 0.0024171 | 1.9633 |  | 54.7755 | 9382.0912 | 0.0024223 | 1.9556 |  | 54.5607 | 9345.297 | 0.0024268 | 1.9487 |  | 54.3697 | 9312.589 | 0.0024308 | 1.9426 |  | 54.1989 | 9283.3237 | 0.0024344 | 1.9371 |  | 54.0451 | 9256.9857 | 0.0024377 | 1.9321 |  | 53.906 | 9233.1574 | 0.0024406 | 1.9276 |  | 53.7795 | 9211.4969 | 0.0024433 | 1.9234 |  | 53.6641 | 9191.7217 | 0.0024457 | 1.9197 |  | 53.5582 | 9173.5961 | 0.002448 | 1.9162 |  | 53.4609 | 9156.9223 | 0.0024501 | 1.9129 |  | 53.371 | 9141.5326
44 |  | Concrete | 12 | 27.9 |  |  | 38.3079 | 171.4756 |  |  | 0.0023486 | 2.0615 |  | 57.5151 | 9862.428 |  | 0.0023111 | 2.1113 |  | 58.9047 | 10100.7169 |  | 0.0022491 | 2.1879 |  | 61.0424 | 10467.2811 |  | 0.0023486 | 2.0615 |  | 57.5151 | 9862.428 |  | 0.0023651 | 2.0386 |  | 56.8782 | 9753.2217 | 0.0023783 | 2.0199 |  | 56.356 | 9663.6848 | 0.0023892 | 2.0043 |  | 55.9204 | 9588.9763 | 0.0023983 | 1.9911 |  | 55.5514 | 9525.7131 | 0.0024061 | 1.9798 |  | 55.2351 | 9471.4632 | 0.0024127 | 1.9699 |  | 54.9608 | 9424.4353 | 0.0024184 | 1.9613 |  | 54.7208 | 9383.2815 | 0.0024235 | 1.9537 |  | 54.509 | 9346.9687 | 0.0024279 | 1.947 |  | 54.3208 | 9314.6921 | 0.0024319 | 1.9409 |  | 54.1524 | 9285.8154 | 0.0024355 | 1.9355 |  | 54.0009 | 9259.8293 | 0.0024387 | 1.9306 |  | 53.8638 | 9236.3211 | 0.0024416 | 1.9261 |  | 53.7392 | 9214.953 | 0.0024442 | 1.9221 |  | 53.6254 | 9195.4459 | 0.0024466 | 1.9183 |  | 53.5211 | 9177.567 | 0.0024488 | 1.9149 |  | 53.4252 | 9161.1208 | 0.0024508 | 1.9117 |  | 53.3367 | 9145.942
45 |  | Concrete | 13 | 27.9 |  |  | 35.9157 | 171.6685 |  |  | 0.002351 | 2.0581 |  | 57.4223 | 9857.6049 |  | 0.0023142 | 2.1073 |  | 58.795 | 10093.2565 |  | 0.0022532 | 2.1832 |  | 60.9099 | 10456.3179 |  | 0.002351 | 2.0581 |  | 57.4223 | 9857.6049 |  | 0.0023672 | 2.0356 |  | 56.7937 | 9749.6873 | 0.0023803 | 2.0171 |  | 56.2785 | 9661.2411 | 0.002391 | 2.0017 |  | 55.8487 | 9587.465 | 0.0024 | 1.9887 |  | 55.4849 | 9525.0065 | 0.0024076 | 1.9775 |  | 55.173 | 9471.4574 | 0.0024141 | 1.9678 |  | 54.9026 | 9425.0447 | 0.0024197 | 1.9594 |  | 54.666 | 9384.435 | 0.0024247 | 1.9519 |  | 54.4573 | 9348.6067 | 0.0024291 | 1.9452 |  | 54.2718 | 9316.764 | 0.002433 | 1.9393 |  | 54.1059 | 9288.2783 | 0.0024365 | 1.9339 |  | 53.9566 | 9262.6461 | 0.0024396 | 1.9291 |  | 53.8215 | 9239.4597 | 0.0024425 | 1.9247 |  | 53.6988 | 9218.3855 | 0.0024451 | 1.9207 |  | 53.5867 | 9199.1478 | 0.0024475 | 1.917 |  | 53.484 | 9181.5168 | 0.0024496 | 1.9136 |  | 53.3895 | 9165.2995 | 0.0024516 | 1.9105 |  | 53.3023 | 9150.3325
46 |  | Concrete | 14 | 27.9 |  |  | 33.5234 | 171.8614 |  |  | 0.0023534 | 2.0548 |  | 57.3293 | 9852.6919 |  | 0.0023172 | 2.1034 |  | 58.6849 | 10085.6698 |  | 0.0022572 | 2.1784 |  | 60.7766 | 10445.1552 |  | 0.0023534 | 2.0548 |  | 57.3293 | 9852.6919 |  | 0.0023694 | 2.0326 |  | 56.7089 | 9746.0773 | 0.0023822 | 2.0144 |  | 56.2007 | 9658.7326 | 0.0023928 | 1.9992 |  | 55.7769 | 9585.8971 | 0.0024016 | 1.9863 |  | 55.4182 | 9524.2499 | 0.0024091 | 1.9753 |  | 55.1107 | 9471.4069 | 0.0024155 | 1.9657 |  | 54.8443 | 9425.6137 | 0.0024211 | 1.9574 |  | 54.6112 | 9385.5517 | 0.0024259 | 1.95 |  | 54.4055 | 9350.2109 | 0.0024303 | 1.9435 |  | 54.2228 | 9318.8049 | 0.0024341 | 1.9376 |  | 54.0593 | 9290.7123 | 0.0024375 | 1.9323 |  | 53.9123 | 9265.436 | 0.0024406 | 1.9276 |  | 53.7792 | 9242.5732 | 0.0024434 | 1.9232 |  | 53.6583 | 9221.7944 | 0.002446 | 1.9193 |  | 53.548 | 9202.8275 | 0.0024483 | 1.9157 |  | 53.4468 | 9185.4456 | 0.0024505 | 1.9123 |  | 53.3538 | 9169.4582 | 0.0024524 | 1.9092 |  | 53.2679 | 9154.704
47 |  | Concrete | 15 | 27.9 |  |  | 31.1312 | 172.0543 |  |  | 0.0023558 | 2.0515 |  | 57.2359 | 9847.689 |  | 0.0023202 | 2.0994 |  | 58.5743 | 10077.9565 |  | 0.0022612 | 2.1736 |  | 60.6424 | 10433.7926 |  | 0.0023558 | 2.0515 |  | 57.2359 | 9847.689 |  | 0.0023716 | 2.0295 |  | 56.6239 | 9742.3917 | 0.0023842 | 2.0116 |  | 56.1227 | 9656.1592 | 0.0023946 | 1.9966 |  | 55.7049 | 9584.2726 | 0.0024032 | 1.9839 |  | 55.3514 | 9523.4432 | 0.0024106 | 1.9731 |  | 55.0484 | 9471.3115 | 0.0024169 | 1.9637 |  | 54.7859 | 9426.1422 | 0.0024224 | 1.9554 |  | 54.5562 | 9386.6316 | 0.0024272 | 1.9482 |  | 54.3537 | 9351.7814 | 0.0024314 | 1.9417 |  | 54.1737 | 9320.8146 | 0.0024352 | 1.9359 |  | 54.0127 | 9293.1175 | 0.0024386 | 1.9307 |  | 53.8679 | 9268.1989 | 0.0024416 | 1.9261 |  | 53.7369 | 9245.6614 | 0.0024444 | 1.9218 |  | 53.6178 | 9225.1796 | 0.0024469 | 1.9179 |  | 53.5092 | 9206.4849 | 0.0024492 | 1.9143 |  | 53.4096 | 9189.3533 | 0.0024513 | 1.911 |  | 53.318 | 9173.5969 | 0.0024532 | 1.908 |  | 53.2335 | 9159.0566
48 |  | Concrete | 16 | 27.9 |  |  | 28.739 | 172.2472 |  |  | 0.0023583 | 2.0481 |  | 57.1423 | 9842.5959 |  | 0.0023232 | 2.0955 |  | 58.4631 | 10070.1163 |  | 0.0022652 | 2.1687 |  | 60.5074 | 10422.2297 |  | 0.0023583 | 2.0481 |  | 57.1423 | 9842.5959 |  | 0.0023737 | 2.0265 |  | 56.5387 | 9738.6304 | 0.0023861 | 2.0088 |  | 56.0446 | 9653.5207 | 0.0023963 | 1.994 |  | 55.6328 | 9582.5914 | 0.0024049 | 1.9815 |  | 55.2844 | 9522.5863 | 0.0024121 | 1.9708 |  | 54.9859 | 9471.1712 | 0.0024183 | 1.9616 |  | 54.7273 | 9426.6302 | 0.0024237 | 1.9534 |  | 54.5012 | 9387.6745 | 0.0024284 | 1.9463 |  | 54.3017 | 9353.318 | 0.0024326 | 1.9399 |  | 54.1245 | 9322.7931 | 0.0024363 | 1.9343 |  | 53.966 | 9295.4937 | 0.0024396 | 1.9292 |  | 53.8234 | 9270.9349 | 0.0024426 | 1.9245 |  | 53.6945 | 9248.7244 | 0.0024453 | 1.9203 |  | 53.5773 | 9228.5411 | 0.0024478 | 1.9165 |  | 53.4703 | 9210.1199 | 0.00245 | 1.913 |  | 53.3723 | 9193.2399 | 0.0024521 | 1.9098 |  | 53.2822 | 9177.7156 | 0.002454 | 1.9068 |  | 53.1991 | 9163.3902
49 |  | Concrete | 17 | 27.9 |  |  | 26.3467 | 172.4402 |  |  | 0.0023607 | 2.0447 |  | 57.0483 | 9837.4125 |  | 0.0023263 | 2.0915 |  | 58.3515 | 10062.1488 |  | 0.0022692 | 2.1639 |  | 60.3715 | 10410.4659 |  | 0.0023607 | 2.0447 |  | 57.0483 | 9837.4125 |  | 0.0023759 | 2.0234 |  | 56.4532 | 9734.7931 | 0.0023881 | 2.006 |  | 55.9662 | 9650.8171 | 0.0023981 | 1.9914 |  | 55.5605 | 9580.8533 | 0.0024065 | 1.9791 |  | 55.2173 | 9521.6791 | 0.0024136 | 1.9686 |  | 54.9233 | 9470.9859 | 0.0024197 | 1.9595 |  | 54.6687 | 9427.0775 | 0.002425 | 1.9515 |  | 54.446 | 9388.6805 | 0.0024296 | 1.9444 |  | 54.2497 | 9354.8208 | 0.0024337 | 1.9382 |  | 54.0752 | 9324.7403 | 0.0024374 | 1.9326 |  | 53.9192 | 9297.8409 | 0.0024406 | 1.9276 |  | 53.7789 | 9273.6439 | 0.0024436 | 1.923 |  | 53.652 | 9251.7622 | 0.0024462 | 1.9189 |  | 53.5367 | 9231.8789 | 0.0024487 | 1.9151 |  | 53.4315 | 9213.7326 | 0.0024509 | 1.9117 |  | 53.3351 | 9197.1054 | 0.0024529 | 1.9085 |  | 53.2464 | 9181.8143 | 0.0024548 | 1.9055 |  | 53.1646 | 9167.7047
50 |  | Concrete | 18 | 27.9 |  |  | 23.9545 | 172.6331 |  |  | 0.0023631 | 2.0414 |  | 56.954 | 9832.1385 |  | 0.0023293 | 2.0874 |  | 58.2394 | 10054.0539 |  | 0.0022733 | 2.1589 |  | 60.2347 | 10398.5007 |  | 0.0023631 | 2.0414 |  | 56.954 | 9832.1385 |  | 0.0023781 | 2.0203 |  | 56.3674 | 9730.8797 | 0.00239 | 2.0031 |  | 55.8876 | 9648.0482 | 0.0023999 | 1.9888 |  | 55.488 | 9579.0582 | 0.0024081 | 1.9767 |  | 55.15 | 9520.7216 | 0.0024151 | 1.9663 |  | 54.8606 | 9470.7556 | 0.0024211 | 1.9573 |  | 54.6099 | 9427.4842 | 0.0024263 | 1.9495 |  | 54.3908 | 9389.6495 | 0.0024308 | 1.9426 |  | 54.1975 | 9356.2896 | 0.0024349 | 1.9364 |  | 54.0259 | 9326.6562 | 0.0024385 | 1.9309 |  | 53.8724 | 9300.159 | 0.0024417 | 1.926 |  | 53.7343 | 9276.3259 | 0.0024446 | 1.9215 |  | 53.6095 | 9254.7747 | 0.0024472 | 1.9174 |  | 53.4961 | 9235.193 | 0.0024496 | 1.9137 |  | 53.3926 | 9217.323 | 0.0024517 | 1.9103 |  | 53.2977 | 9200.9498 | 0.0024537 | 1.9072 |  | 53.2105 | 9185.893 | 0.0024556 | 1.9043 |  | 53.13 | 9172.0002
51 |  | Concrete | 19 | 27.9 |  |  | 21.5623 | 172.826 |  |  | 0.0023656 | 2.038 |  | 56.8593 | 9826.7738 |  | 0.0023323 | 2.0834 |  | 58.1268 | 10045.8312 |  | 0.0022773 | 2.154 |  | 60.0971 | 10386.3336 |  | 0.0023656 | 2.038 |  | 56.8593 | 9826.7738 |  | 0.0023802 | 2.0173 |  | 56.2814 | 9726.8901 | 0.002392 | 2.0003 |  | 55.8088 | 9645.214 | 0.0024017 | 1.9862 |  | 55.4153 | 9577.2062 | 0.0024097 | 1.9743 |  | 55.0826 | 9519.7136 | 0.0024166 | 1.9641 |  | 54.7978 | 9470.4802 | 0.0024225 | 1.9552 |  | 54.5511 | 9427.8501 | 0.0024276 | 1.9475 |  | 54.3355 | 9390.5814 | 0.0024321 | 1.9407 |  | 54.1453 | 9357.7244 | 0.002436 | 1.9346 |  | 53.9765 | 9328.5408 | 0.0024395 | 1.9292 |  | 53.8255 | 9302.4482 | 0.0024427 | 1.9244 |  | 53.6897 | 9278.9808 | 0.0024455 | 1.92 |  | 53.5669 | 9257.7618 | 0.0024481 | 1.916 |  | 53.4554 | 9238.4833 | 0.0024505 | 1.9123 |  | 53.3536 | 9220.8909 | 0.0024526 | 1.909 |  | 53.2603 | 9204.773 | 0.0024546 | 1.9059 |  | 53.1746 | 9189.9517 | 0.0024564 | 1.9031 |  | 53.0955 | 9176.2767
52 |  | Concrete | 20 | 27.9 |  |  | 19.17 | 173.0189 |  |  | 0.002368 | 2.0346 |  | 56.7644 | 9821.3182 |  | 0.0023354 | 2.0793 |  | 58.0138 | 10037.4805 |  | 0.0022813 | 2.1491 |  | 59.9585 | 10373.9641 |  | 0.002368 | 2.0346 |  | 56.7644 | 9821.3182 |  | 0.0023824 | 2.0142 |  | 56.1951 | 9722.8242 | 0.0023939 | 1.9975 |  | 55.7298 | 9642.3142 | 0.0024034 | 1.9836 |  | 55.3425 | 9575.297 | 0.0024114 | 1.9719 |  | 55.0151 | 9518.6552 | 0.0024181 | 1.9618 |  | 54.7348 | 9470.1596 | 0.0024239 | 1.9531 |  | 54.4922 | 9428.1753 | 0.0024289 | 1.9455 |  | 54.28 | 9391.4762 | 0.0024333 | 1.9388 |  | 54.0931 | 9359.1252 | 0.0024372 | 1.9329 |  | 53.927 | 9330.394 | 0.0024406 | 1.9275 |  | 53.7786 | 9304.7082 | 0.0024437 | 1.9228 |  | 53.645 | 9281.6086 | 0.0024465 | 1.9184 |  | 53.5243 | 9260.7236 | 0.0024491 | 1.9145 |  | 53.4147 | 9241.7498 | 0.0024514 | 1.9109 |  | 53.3146 | 9224.4365 | 0.0024535 | 1.9076 |  | 53.2229 | 9208.575 | 0.0024554 | 1.9046 |  | 53.1386 | 9193.9902 | 0.0024571 | 1.9018 |  | 53.0609 | 9180.5341
53 |  | Concrete | 21 | 32 |  |  | 14.3084 | 177.424 |  |  | 0.0024234 | 1.9538 |  | 62.5219 | 11092.88 |  | 0.0024045 | 1.982 |  | 63.4251 | 11253.1348 |  | 0.0023732 | 2.0273 |  | 64.8732 | 11510.0624 |  | 0.0024234 | 1.9538 |  | 62.5219 | 11092.88 |  | 0.0024318 | 1.9411 |  | 62.1164 | 11020.9395 | 0.0024385 | 1.9309 |  | 61.7876 | 10962.5982 | 0.002444 | 1.9224 |  | 61.5156 | 10914.3378 | 0.0024486 | 1.9152 |  | 61.2868 | 10873.7558 | 0.0024525 | 1.9091 |  | 61.0918 | 10839.1564 | 0.0024559 | 1.9039 |  | 60.9236 | 10809.3084 | 0.0024588 | 1.8993 |  | 60.777 | 10783.2966 | 0.0024613 | 1.8953 |  | 60.6481 | 10760.4265 | 0.0024636 | 1.8917 |  | 60.5339 | 10740.1615 | 0.0024656 | 1.8885 |  | 60.432 | 10722.0808 | 0.0024674 | 1.8856 |  | 60.3405 | 10705.8494 | 0.002469 | 1.8831 |  | 60.2579 | 10691.1974 | 0.0024704 | 1.8807 |  | 60.183 | 10677.9052 | 0.0024718 | 1.8786 |  | 60.1147 | 10665.7918 | 0.002473 | 1.8766 |  | 60.0522 | 10654.7071 | 0.0024741 | 1.8748 |  | 59.9949 | 10644.5256 | 0.0024751 | 1.8732 |  | 59.942 | 10635.141
54 |  | Concrete | 22 | 32 |  |  | 13.9868 | 173.4369 |  |  | 0.0023733 | 2.0272 |  | 64.869 | 11250.6781 |  | 0.0023419 | 2.0705 |  | 66.2562 | 11491.2649 |  | 0.00229 | 2.1382 |  | 68.4221 | 11866.9155 |  | 0.0023733 | 2.0272 |  | 64.869 | 11250.6781 |  | 0.0023871 | 2.0074 |  | 64.2379 | 11141.2209 | 0.0023982 | 1.9913 |  | 63.7224 | 11051.8206 | 0.0024073 | 1.9779 |  | 63.2936 | 10977.4496 | 0.0024149 | 1.9666 |  | 62.9314 | 10914.6243 | 0.0024214 | 1.9569 |  | 62.6214 | 10860.857 | 0.0024269 | 1.9485 |  | 62.3531 | 10814.325 | 0.0024317 | 1.9412 |  | 62.1186 | 10773.6628 | 0.002436 | 1.9348 |  | 61.912 | 10737.8274 | 0.0024397 | 1.929 |  | 61.7285 | 10706.0089 | 0.002443 | 1.9239 |  | 61.5646 | 10677.5685 | 0.002446 | 1.9193 |  | 61.4171 | 10651.996 | 0.0024487 | 1.9151 |  | 61.2838 | 10628.8789 | 0.0024511 | 1.9113 |  | 61.1628 | 10607.8801 | 0.0024533 | 1.9079 |  | 61.0523 | 10588.7214 | 0.0024553 | 1.9047 |  | 60.9511 | 10571.1712 | 0.0024572 | 1.9018 |  | 60.8581 | 10555.0354 | 0.0024589 | 1.8991 |  | 60.7722 | 10540.1497
55 |  | Concrete | 23 | 32 |  |  | 13.6653 | 169.4499 |  |  | 0.0023231 | 2.0957 |  | 67.0621 | 11363.6636 |  | 0.0022793 | 2.1515 |  | 68.8477 | 11666.2291 |  | 0.0022069 | 2.2359 |  | 71.5483 | 12123.8518 |  | 0.0023231 | 2.0957 |  | 67.0621 | 11363.6636 |  | 0.0023424 | 2.0699 |  | 66.2371 | 11223.87 | 0.0023579 | 2.0487 |  | 65.5579 | 11108.7725 | 0.0023706 | 2.0309 |  | 64.9893 | 11012.4218 | 0.0023812 | 2.0158 |  | 64.5065 | 10930.6178 | 0.0023902 | 2.0029 |  | 64.0916 | 10860.3179 | 0.002398 | 1.9916 |  | 63.7313 | 10799.2673 | 0.0024047 | 1.9817 |  | 63.4156 | 10745.7611 | 0.0024106 | 1.973 |  | 63.1366 | 10698.4875 | 0.0024158 | 1.9653 |  | 62.8883 | 10656.4209 | 0.0024204 | 1.9583 |  | 62.666 | 10618.7483 | 0.0024246 | 1.9521 |  | 62.4658 | 10584.8171 | 0.0024283 | 1.9464 |  | 62.2845 | 10554.0976 | 0.0024317 | 1.9412 |  | 62.1196 | 10526.1552 | 0.0024348 | 1.9365 |  | 61.9689 | 10500.6304 | 0.0024376 | 1.9322 |  | 61.8308 | 10477.2229 | 0.0024402 | 1.9282 |  | 61.7037 | 10455.68 | 0.0024426 | 1.9246 |  | 61.5863 | 10435.7879
56 |  | Concrete | 24 | 32 |  |  | 13.3438 | 165.4628 |  |  | 0.0022729 | 2.1594 |  | 69.1012 | 11433.6785 |  | 0.0022168 | 2.225 |  | 71.1996 | 11780.8927 |  | 0.0021238 | 2.3204 |  | 74.2519 | 12285.9266 |  | 0.0022729 | 2.1594 |  | 69.1012 | 11433.6785 |  | 0.0022977 | 2.1286 |  | 68.1141 | 11270.3491 | 0.0023175 | 2.1029 |  | 67.2939 | 11134.6426 | 0.0023339 | 2.0813 |  | 66.6025 | 11020.2397 | 0.0023475 | 2.0629 |  | 66.0122 | 10922.5664 | 0.0023591 | 2.047 |  | 65.5026 | 10838.2479 | 0.0023691 | 2.0331 |  | 65.0584 | 10764.7475 | 0.0023777 | 2.0209 |  | 64.6679 | 10700.1259 | 0.0023852 | 2.0101 |  | 64.3219 | 10642.8771 | 0.0023919 | 2.0004 |  | 64.0133 | 10591.8148 | 0.0023979 | 1.9918 |  | 63.7363 | 10545.9928 | 0.0024032 | 1.984 |  | 63.4865 | 10504.6474 | 0.002408 | 1.9769 |  | 63.2599 | 10467.1558 | 0.0024123 | 1.9704 |  | 63.0535 | 10433.0051 | 0.0024163 | 1.9645 |  | 62.8647 | 10401.7691 | 0.0024199 | 1.9591 |  | 62.6914 | 10373.091 | 0.0024232 | 1.9541 |  | 62.5317 | 10346.6699 | 0.0024263 | 1.9495 |  | 62.3841 | 10322.2499
57 |  | Concrete | 25 | 62.525 |  |  | 12.8534 | 159.3826 |  |  | 0.0021964 | 2.2473 |  | 140.5138 | 22395.4518 |  | 0.0021213 | 2.3227 |  | 145.2245 | 23146.2447 |  | 0.001997 | 2.4238 |  | 151.5472 | 24153.9723 |  | 0.0021964 | 2.2473 |  | 140.5138 | 22395.4518 |  | 0.0022295 | 2.2107 |  | 138.2215 | 22030.0959 | 0.0022561 | 2.1797 |  | 136.2851 | 21721.4622 | 0.0022779 | 2.1533 |  | 134.6321 | 21458.0156 | 0.0022962 | 2.1305 |  | 133.2071 | 21230.8961 | 0.0023116 | 2.1106 |  | 131.9674 | 21033.2953 | 0.0023249 | 2.0932 |  | 130.8797 | 20859.942 | 0.0023365 | 2.0779 |  | 129.9183 | 20706.7137 | 0.0023466 | 2.0642 |  | 129.0628 | 20570.3519 | 0.0023555 | 2.0519 |  | 128.2967 | 20448.2528 | 0.0023635 | 2.0409 |  | 127.6069 | 20338.3143 | 0.0023706 | 2.0309 |  | 126.9827 | 20238.8232 | 0.002377 | 2.0218 |  | 126.4152 | 20148.37 | 0.0023828 | 2.0135 |  | 125.897 | 20065.7857 | 0.0023881 | 2.006 |  | 125.4221 | 19990.093 | 0.0023929 | 1.999 |  | 124.9852 | 19920.4686 | 0.0023974 | 1.9925 |  | 124.5821 | 19856.2148 | 0.0024014 | 1.9865 |  | 124.2089 | 19796.7361
58 |  | Concrete | 26 | 62.525 |  |  | 12.1943 | 151.2091 |  |  | 0.0020935 | 2.3479 |  | 146.8 | 22197.4903 |  | 0.001993 | 2.4265 |  | 151.7188 | 22941.2637 |  | 0.0018266 | 2.5144 |  | 157.2129 | 23772.0271 |  | 0.0020935 | 2.3479 |  | 146.8 | 22197.4903 |  | 0.0021378 | 2.307 |  | 144.2462 | 21811.3429 | 0.0021734 | 2.2715 |  | 142.0246 | 21475.412 | 0.0022027 | 2.2405 |  | 140.0875 | 21182.5 | 0.0022271 | 2.2134 |  | 138.3903 | 20925.8779 | 0.0022478 | 2.1894 |  | 136.895 | 20699.7728 | 0.0022656 | 2.1682 |  | 135.5698 | 20499.3871 | 0.0022811 | 2.1494 |  | 134.3886 | 20320.7788 | 0.0022946 | 2.1324 |  | 133.33 | 20160.7152 | 0.0023066 | 2.1172 |  | 132.3766 | 20016.5398 | 0.0023172 | 2.1034 |  | 131.5136 | 19886.0594 | 0.0023267 | 2.0908 |  | 130.7293 | 19767.4532 | 0.0023353 | 2.0794 |  | 130.0134 | 19659.201 | 0.0023431 | 2.0689 |  | 129.3575 | 19560.0254 | 0.0023502 | 2.0592 |  | 128.7545 | 19468.8469 | 0.0023567 | 2.0504 |  | 128.1983 | 19384.7476 | 0.0023626 | 2.0421 |  | 127.6837 | 19306.943 | 0.002368 | 2.0345 |  | 127.2064 | 19234.7588
59 |  | Concrete | 27 | 62.525 |  |  | 11.5351 | 143.0356 |  |  | 0.0019906 | 2.4282 |  | 151.8215 | 21715.8864 |  | 0.0018647 | 2.4989 |  | 156.2462 | 22348.7736 |  | 0.0016561 | 2.5495 |  | 159.4083 | 22801.0599 |  | 0.0019906 | 2.4282 |  | 151.8215 | 21715.8864 |  | 0.0020462 | 2.3873 |  | 149.2671 | 21350.5197 | 0.0020908 | 2.3502 |  | 146.948 | 21018.8013 | 0.0021274 | 2.3169 |  | 144.8663 | 20721.0356 | 0.002158 | 2.2871 |  | 143.0036 | 20454.6089 | 0.002184 | 2.2605 |  | 141.336 | 20216.0861 | 0.0022063 | 2.2365 |  | 139.8395 | 20002.03 | 0.0022257 | 2.215 |  | 138.4921 | 19809.3013 | 0.0022426 | 2.1955 |  | 137.2745 | 19635.143 | 0.0022576 | 2.1779 |  | 136.1701 | 19477.1771 | 0.002271 | 2.1618 |  | 135.1647 | 19333.3689 | 0.0022829 | 2.1471 |  | 134.2461 | 19201.9818 | 0.0022937 | 2.1336 |  | 133.4041 | 19081.5334 | 0.0023034 | 2.1212 |  | 132.6296 | 18970.7556 | 0.0023123 | 2.1098 |  | 131.9151 | 18868.5606 | 0.0023204 | 2.0992 |  | 131.2541 | 18774.0119 | 0.0023278 | 2.0894 |  | 130.6409 | 18686.3003 | 0.0023347 | 2.0803 |  | 130.0706 | 18604.7237
60 |  | Concrete | 28 | 62.525 |  |  | 10.876 | 134.8622 |  |  | 0.0018877 | 2.4883 |  | 155.5785 | 20981.6489 |  | 0.0017364 | 2.5399 |  | 158.8066 | 21417.005 |  | 0.0014857 | 2.5291 |  | 158.1331 | 21326.1685 |  | 0.0018877 | 2.4883 |  | 155.5785 | 20981.6489 |  | 0.0019545 | 2.4516 |  | 153.2842 | 20672.2406 | 0.0020081 | 2.4159 |  | 151.0553 | 20371.6423 | 0.0020522 | 2.3825 |  | 148.9685 | 20090.2118 | 0.002089 | 2.3518 |  | 147.0469 | 19831.0644 | 0.0021202 | 2.3237 |  | 145.2903 | 19594.1688 | 0.002147 | 2.2981 |  | 143.6888 | 19378.1792 | 0.0021703 | 2.2747 |  | 142.2287 | 19181.2757 | 0.0021906 | 2.2534 |  | 140.8961 | 19001.5516 | 0.0022087 | 2.2339 |  | 139.6773 | 18837.1858 | 0.0022247 | 2.2161 |  | 138.5601 | 18686.5125 | 0.0022391 | 2.1997 |  | 137.5333 | 18548.0414 | 0.002252 | 2.1845 |  | 136.5873 | 18420.4549 | 0.0022637 | 2.1705 |  | 135.7133 | 18302.5948 | 0.0022744 | 2.1576 |  | 134.904 | 18193.4456 | 0.0022841 | 2.1456 |  | 134.1527 | 18092.1174 | 0.002293 | 2.1344 |  | 133.4535 | 17997.83 | 0.0023013 | 2.124 |  | 132.8015 | 17909.8979
61 |  | Concrete | 29 | 62.525 |  |  | 10.2168 | 126.6887 |  |  | 0.0017849 | 2.5281 |  | 158.0708 | 20025.7862 |  | 0.0016081 | 2.5494 |  | 159.4001 | 20194.1888 |  | 0.0013153 | 2.4532 |  | 153.3874 | 19432.4505 |  | 0.0017849 | 2.5281 |  | 158.0708 | 20025.7862 |  | 0.0018629 | 2.4998 |  | 156.2974 | 19801.1201 | 0.0019255 | 2.4686 |  | 154.3464 | 19553.9468 | 0.0019769 | 2.4373 |  | 152.3942 | 19306.6178 | 0.0020199 | 2.4074 |  | 150.5203 | 19069.2193 | 0.0020564 | 2.3792 |  | 148.758 | 18845.9544 | 0.0020877 | 2.3529 |  | 147.1176 | 18638.1434 | 0.0021149 | 2.3286 |  | 145.5986 | 18445.6964 | 0.0021387 | 2.3062 |  | 144.1948 | 18267.8573 | 0.0021597 | 2.2855 |  | 142.8982 | 18103.5868 | 0.0021784 | 2.2663 |  | 141.6998 | 17951.7596 | 0.0021952 | 2.2486 |  | 140.5908 | 17811.2646 | 0.0022103 | 2.2321 |  | 139.563 | 17681.0536 | 0.002224 | 2.2169 |  | 138.6087 | 17560.1616 | 0.0022365 | 2.2027 |  | 137.7211 | 17447.713 | 0.0022478 | 2.1894 |  | 136.894 | 17342.9195 | 0.0022583 | 2.1771 |  | 136.1217 | 17245.0752 | 0.0022679 | 2.1655 |  | 135.3992 | 17153.5488
62 |  | Concrete | 30 | 62.525 |  |  | 9.5577 | 118.5152 |  |  | 0.001682 | 2.5478 |  | 159.2986 | 18879.3067 |  | 0.0014798 | 2.5274 |  | 158.0266 | 18728.5558 |  | 0.0011449 | 2.3218 |  | 145.1712 | 17205.0037 |  | 0.001682 | 2.5478 |  | 159.2986 | 18879.3067 |  | 0.0017712 | 2.5319 |  | 158.3068 | 18761.7727 | 0.0018429 | 2.5081 |  | 156.8214 | 18585.7268 | 0.0019017 | 2.4813 |  | 155.1433 | 18386.8428 | 0.0019508 | 2.4538 |  | 153.4237 | 18183.0488 | 0.0019925 | 2.4269 |  | 151.7389 | 17983.3763 | 0.0020284 | 2.4011 |  | 150.1261 | 17792.2311 | 0.0020594 | 2.3767 |  | 148.6016 | 17611.5576 | 0.0020867 | 2.3538 |  | 147.1708 | 17441.9764 | 0.0021108 | 2.3324 |  | 145.8327 | 17283.4013 | 0.0021322 | 2.3124 |  | 144.5838 | 17135.3798 | 0.0021514 | 2.2938 |  | 143.4186 | 16997.2838 | 0.0021687 | 2.2764 |  | 142.3312 | 16868.4171 | 0.0021843 | 2.2601 |  | 141.3158 | 16748.0745 | 0.0021985 | 2.245 |  | 140.3665 | 16635.5741 | 0.0022116 | 2.2308 |  | 139.4781 | 16530.274 | 0.0022235 | 2.2174 |  | 138.6453 | 16431.5791 | 0.0022345 | 2.2049 |  | 137.8637 | 16338.9436
63 |  | Concrete | 31 | 62.525 |  |  | 8.8985 | 110.3418 |  |  | 0.0015791 | 2.5472 |  | 159.2617 | 17573.2191 |  | 0.0013515 | 2.474 |  | 154.6861 | 17068.3369 |  | 0.00097447 | 2.1349 |  | 133.4846 | 14728.926 |  | 0.0015791 | 2.5472 |  | 159.2617 | 17573.2191 |  | 0.0016795 | 2.548 |  | 159.3124 | 17578.8128 | 0.0017602 | 2.5347 |  | 158.4803 | 17486.9944 | 0.0018264 | 2.5144 |  | 157.2159 | 17347.4763 | 0.0018818 | 2.4911 |  | 155.7572 | 17186.5281 | 0.0019287 | 2.4667 |  | 154.2332 | 17018.3679 | 0.001969 | 2.4424 |  | 152.7142 | 16850.751 | 0.002004 | 2.4188 |  | 151.2379 | 16687.8537 | 0.0020347 | 2.3962 |  | 149.8238 | 16531.8252 | 0.0020618 | 2.3747 |  | 148.4809 | 16383.6503 | 0.0020859 | 2.3545 |  | 147.2121 | 16243.6425 | 0.0021075 | 2.3353 |  | 146.0166 | 16111.7316 | 0.002127 | 2.3173 |  | 144.8919 | 15987.6334 | 0.0021446 | 2.3004 |  | 143.8345 | 15870.952 | 0.0021606 | 2.2845 |  | 142.8402 | 15761.2403 | 0.0021753 | 2.2696 |  | 141.9049 | 15658.0364 | 0.0021887 | 2.2555 |  | 141.0244 | 15560.885 | 0.0022011 | 2.2422 |  | 140.1949 | 15469.3495
64 |  | Concrete | 32 | 62.525 |  |  | 8.2394 | 102.1683 |  |  | 0.0014763 | 2.5264 |  | 157.9603 | 16138.5318 |  | 0.0012232 | 2.3891 |  | 149.3786 | 15261.7628 |  | 0.00080405 | 1.8925 |  | 118.3275 | 12089.3151 |  | 0.0014763 | 2.5264 |  | 157.9603 | 16138.5318 |  | 0.0015879 | 2.548 |  | 159.3141 | 16276.8549 | 0.0016776 | 2.5481 |  | 159.323 | 16277.7614 | 0.0017512 | 2.5368 |  | 158.6119 | 16205.1075 | 0.0018127 | 2.5193 |  | 157.5208 | 16093.6321 | 0.0018649 | 2.4989 |  | 156.2408 | 15962.8627 | 0.0019097 | 2.4771 |  | 154.8818 | 15824.0116 | 0.0019486 | 2.4551 |  | 153.5073 | 15683.5791 | 0.0019827 | 2.4335 |  | 152.154 | 15545.32 | 0.0020129 | 2.4125 |  | 150.8428 | 15411.3548 | 0.0020397 | 2.3924 |  | 149.5847 | 15282.8174 | 0.0020637 | 2.3732 |  | 148.385 | 15160.2404 | 0.0020853 | 2.355 |  | 147.2452 | 15043.7903 | 0.0021049 | 2.3377 |  | 146.1648 | 14933.4127 | 0.0021227 | 2.3213 |  | 145.1421 | 14828.9228 | 0.002139 | 2.3059 |  | 144.1745 | 14730.0623 | 0.0021539 | 2.2912 |  | 143.2591 | 14636.536 | 0.0021677 | 2.2774 |  | 142.3928 | 14548.0338
65 |  | Concrete | 33 | 62.525 |  |  | 7.5802 | 93.9948 |  |  | 0.0013734 | 2.4853 |  | 155.3942 | 14606.2533 |  | 0.0010949 | 2.2728 |  | 142.1042 | 13357.0644 |  | 0.00063364 | 1.5946 |  | 99.6998 | 9371.2688 |  | 0.0013734 | 2.4853 |  | 155.3942 | 14606.2533 |  | 0.0014962 | 2.532 |  | 158.312 | 14880.5133 | 0.0015949 | 2.5486 |  | 159.3496 | 14978.0399 | 0.001676 | 2.5483 |  | 159.3314 | 14976.3257 | 0.0017437 | 2.5384 |  | 158.7144 | 14918.336 | 0.0018011 | 2.5232 |  | 157.7618 | 14828.7943 | 0.0018504 | 2.5051 |  | 156.629 | 14722.3216 | 0.0018932 | 2.4856 |  | 155.4099 | 14607.7282 | 0.0019308 | 2.4656 |  | 154.1614 | 14490.377 | 0.0019639 | 2.4457 |  | 152.9184 | 14373.536 | 0.0019934 | 2.4263 |  | 151.7017 | 14259.1739 | 0.0020198 | 2.4074 |  | 150.5236 | 14148.4427 | 0.0020436 | 2.3893 |  | 149.3909 | 14041.9756 | 0.0020652 | 2.372 |  | 148.3068 | 13940.0751 | 0.0020848 | 2.3554 |  | 147.2723 | 13842.8329 | 0.0021027 | 2.3397 |  | 146.2868 | 13750.2075 | 0.0021192 | 2.3247 |  | 145.3492 | 13662.0753 | 0.0021343 | 2.3104 |  | 144.4575 | 13578.2637
66 |  | Concrete | 34 | 62.525 |  |  | 6.9211 | 85.8214 |  |  | 0.0012705 | 2.424 |  | 151.5635 | 13007.3921 |  | 0.00096663 | 2.125 |  | 132.8628 | 11402.4724 |  | 0.00046322 | 1.2411 |  | 77.6017 | 6659.8848 |  | 0.0012705 | 2.424 |  | 151.5635 | 13007.3921 |  | 0.0014046 | 2.4999 |  | 156.3061 | 13414.4027 | 0.0015123 | 2.5359 |  | 158.56 | 13607.8417 | 0.0016007 | 2.549 |  | 159.3743 | 13677.7202 | 0.0016746 | 2.5484 |  | 159.3381 | 13674.615 | 0.0017373 | 2.5397 |  | 158.7961 | 13628.096 | 0.0017911 | 2.5263 |  | 157.9559 | 13555.9896 | 0.0018378 | 2.5101 |  | 156.9457 | 13469.2952 | 0.0018788 | 2.4925 |  | 155.8459 | 13374.9127 | 0.001915 | 2.4743 |  | 154.7075 | 13277.2149 | 0.0019472 | 2.456 |  | 153.5629 | 13178.9815 | 0.001976 | 2.4379 |  | 152.4325 | 13081.971 | 0.002002 | 2.4203 |  | 151.3292 | 12987.2772 | 0.0020255 | 2.4032 |  | 150.2604 | 12895.5578 | 0.0020469 | 2.3867 |  | 149.2307 | 12807.182 | 0.0020665 | 2.3709 |  | 148.2419 | 12722.3275 | 0.0020844 | 2.3558 |  | 147.2948 | 12641.0461 | 0.0021009 | 2.3413 |  | 146.389 | 12563.3065
67 |  | Concrete | 35 | 62.525 |  |  | 6.2619 | 77.6479 |  |  | 0.0011676 | 2.3426 |  | 146.4683 | 11372.9568 |  | 0.00083833 | 1.9457 |  | 121.6545 | 9446.2178 |  | 0.0002928 | 0.8322 |  | 52.0331 | 4040.261 |  | 0.0011676 | 2.3426 |  | 146.4683 | 11372.9568 |  | 0.0013129 | 2.4518 |  | 153.2963 | 11903.1373 | 0.0014296 | 2.5103 |  | 156.9544 | 12187.179 | 0.0015255 | 2.5388 |  | 158.7407 | 12325.8802 | 0.0016055 | 2.5492 |  | 159.3918 | 12376.4441 | 0.0016735 | 2.5485 |  | 159.3436 | 12372.7014 | 0.0017318 | 2.5408 |  | 158.8623 | 12335.3242 | 0.0017824 | 2.5288 |  | 158.1147 | 12277.2745 | 0.0018268 | 2.5143 |  | 157.2076 | 12206.8432 | 0.001866 | 2.4984 |  | 156.2104 | 12129.4125 | 0.0019009 | 2.4817 |  | 155.1685 | 12048.5098 | 0.0019322 | 2.4648 |  | 154.1118 | 11966.4578 | 0.0019603 | 2.448 |  | 153.0599 | 11884.7829 | 0.0019858 | 2.4314 |  | 152.0257 | 11804.4793 | 0.002009 | 2.4153 |  | 151.0173 | 11726.1812 | 0.0020302 | 2.3997 |  | 150.0398 | 11650.278 | 0.0020496 | 2.3846 |  | 149.096 | 11576.9916 | 0.0020675 | 2.37 |  | 148.1872 | 11506.4294
68 |  | Concrete | 36 | 62.525 |  |  | 5.6028 | 69.4744 |  |  | 0.0010648 | 2.2408 |  | 140.1084 | 9733.9559 |  | 0.00071003 | 1.735 |  | 108.4792 | 7536.5312 |  | 0.00012238 | 0.36776 |  | 22.994 | 1597.495 |  | 0.0010648 | 2.2408 |  | 140.1084 | 9733.9559 |  | 0.0012213 | 2.3876 |  | 149.2827 | 10371.3316 | 0.001347 | 2.4715 |  | 154.5326 | 10736.0637 | 0.0014502 | 2.5179 |  | 157.4305 | 10937.3951 | 0.0015365 | 2.541 |  | 158.8757 | 11037.7985 | 0.0016096 | 2.5495 |  | 159.4046 | 11074.5438 | 0.0016725 | 2.5486 |  | 159.3483 | 11070.634 | 0.001727 | 2.5417 |  | 158.9169 | 11040.6605 | 0.0017748 | 2.5309 |  | 158.2465 | 10994.085 | 0.0018171 | 2.5178 |  | 157.4269 | 10937.1499 | 0.0018546 | 2.5033 |  | 156.5184 | 10874.0283 | 0.0018883 | 2.488 |  | 155.5613 | 10807.5356 | 0.0019186 | 2.4723 |  | 154.5832 | 10739.5806 | 0.0019461 | 2.4567 |  | 153.6026 | 10671.4581 | 0.0019711 | 2.4411 |  | 152.6323 | 10604.042 | 0.0019939 | 2.4259 |  | 151.6804 | 10537.9146 | 0.0020148 | 2.4111 |  | 150.7526 | 10473.4549 | 0.0020341 | 2.3967 |  | 149.8522 | 10410.8997
69 |  | Concrete | 37 | 62.525 |  |  | 4.9436 | 61.301 |  |  | 0.00096189 | 2.1189 |  | 132.484 | 8121.3978 |  | 0.00058173 | 1.4928 |  | 93.3369 | 5721.6436 |  | -4.804e-05 | 0 |  | 0 | 0 |  | 0.00096189 | 2.1189 |  | 132.484 | 8121.3978 |  | 0.0011296 | 2.3073 |  | 144.2652 | 8843.6002 | 0.0012644 | 2.4197 |  | 151.2946 | 9274.5077 | 0.001375 | 2.4861 |  | 155.4437 | 9528.8542 | 0.0014674 | 2.5236 |  | 157.7895 | 9672.6532 | 0.0015458 | 2.5426 |  | 158.9788 | 9745.5568 | 0.0016132 | 2.5496 |  | 159.4139 | 9772.2275 | 0.0016716 | 2.5486 |  | 159.3522 | 9768.4475 | 0.0017228 | 2.5424 |  | 158.9624 | 9744.5542 | 0.0017681 | 2.5327 |  | 158.3571 | 9707.4481 | 0.0018084 | 2.5208 |  | 157.6126 | 9661.8065 | 0.0018445 | 2.5075 |  | 156.7811 | 9610.8369 | 0.001877 | 2.4934 |  | 155.8989 | 9556.7581 | 0.0019064 | 2.4789 |  | 154.9912 | 9501.1128 | 0.0019332 | 2.4642 |  | 154.0754 | 9444.9756 | 0.0019576 | 2.4496 |  | 153.1638 | 9389.0928 | 0.0019801 | 2.4353 |  | 152.2648 | 9333.9794 | 0.0020007 | 2.4212 |  | 151.3839 | 9279.9846
70 |  | Concrete | 38 | 62.525 |  |  | 4.2845 | 53.1275 |  |  | 0.00085902 | 1.9767 |  | 123.5949 | 6566.2911 |  | 0.00045343 | 1.2192 |  | 76.2276 | 4049.7857 |  | -0.00021846 | 0 |  | 0 | 0 |  | 0.00085902 | 1.9767 |  | 123.5949 | 6566.2911 |  | 0.001038 | 2.211 |  | 138.2439 | 7344.5573 | 0.0011817 | 2.3549 |  | 147.2405 | 7822.523 | 0.0012997 | 2.4435 |  | 152.7805 | 8116.8468 | 0.0013984 | 2.4971 |  | 156.1335 | 8294.9834 | 0.001482 | 2.5281 |  | 158.0664 | 8397.6739 | 0.0015538 | 2.5439 |  | 159.0591 | 8450.4135 | 0.0016162 | 2.5497 |  | 159.4208 | 8469.6299 | 0.0016709 | 2.5487 |  | 159.3556 | 8466.1671 | 0.0017192 | 2.543 |  | 159.001 | 8447.3283 | 0.0017621 | 2.5342 |  | 158.4511 | 8418.1139 | 0.0018006 | 2.5233 |  | 157.7712 | 8381.9942 | 0.0018353 | 2.5111 |  | 157.0072 | 8341.4033 | 0.0018667 | 2.4981 |  | 156.1914 | 8298.0619 | 0.0018953 | 2.4846 |  | 155.3469 | 8253.1932 | 0.0019214 | 2.4709 |  | 154.49 | 8207.6685 | 0.0019453 | 2.4571 |  | 153.6324 | 8162.1081 | 0.0019673 | 2.4435 |  | 152.7824 | 8116.9514
71 |  | Concrete | 39 | 62.525 |  |  | 3.6253 | 44.9541 |  |  | 0.00075614 | 1.8143 |  | 113.4413 | 5099.6443 |  | 0.00032513 | 0.91406 |  | 57.1514 | 2569.1884 |  | -0.00038888 | 0 |  | 0 | 0 |  | 0.00075614 | 1.8143 |  | 113.4413 | 5099.6443 |  | 0.00094631 | 2.0987 |  | 131.2188 | 5898.8176 | 0.0010991 | 2.277 |  | 142.3703 | 6400.1216 | 0.0012245 | 2.3901 |  | 149.4406 | 6717.9621 | 0.0013293 | 2.4615 |  | 153.9075 | 6918.7642 | 0.0014182 | 2.5057 |  | 156.6673 | 7042.8284 | 0.0014945 | 2.5315 |  | 158.2838 | 7115.5005 | 0.0015608 | 2.5449 |  | 159.1225 | 7153.202 | 0.0016189 | 2.5498 |  | 159.4259 | 7166.8401 | 0.0016702 | 2.5487 |  | 159.3585 | 7163.8114 | 0.0017159 | 2.5435 |  | 159.0339 | 7149.22 | 0.0017568 | 2.5355 |  | 158.5316 | 7126.64 | 0.0017936 | 2.5255 |  | 157.908 | 7098.6039 | 0.001827 | 2.5142 |  | 157.2033 | 7066.924 | 0.0018573 | 2.5021 |  | 156.4465 | 7032.9062 | 0.0018851 | 2.4895 |  | 155.6589 | 6997.4971 | 0.0019105 | 2.4767 |  | 154.8555 | 6961.3842 | 0.0019339 | 2.4638 |  | 154.0477 | 6925.0673
72 |  | Concrete | 40 | 62.525 |  |  | 2.9662 | 36.7806 |  |  | 0.00065327 | 1.6317 |  | 102.023 | 3752.4658 |  | 0.00019684 | 0.5775 |  | 36.1082 | 1328.0824 |  | -0.0005593 | 0 |  | 0 | 0 |  | 0.00065327 | 1.6317 |  | 102.023 | 3752.4658 |  | 0.00085465 | 1.9702 |  | 123.1899 | 4530.9954 | 0.0010164 | 2.1861 |  | 136.6839 | 5027.3154 | 0.0011492 | 2.3259 |  | 145.4242 | 5348.7895 | 0.0012602 | 2.4168 |  | 151.1115 | 5557.9706 | 0.0013544 | 2.4755 |  | 154.7815 | 5692.9538 | 0.0014352 | 2.5124 |  | 157.0882 | 5777.797 | 0.0015054 | 2.5343 |  | 158.4574 | 5828.1582 | 0.0015669 | 2.5458 |  | 159.1733 | 5854.4895 | 0.0016213 | 2.5499 |  | 159.4297 | 5863.9185 | 0.0016696 | 2.5488 |  | 159.3611 | 5861.3943 | 0.0017129 | 2.544 |  | 159.0623 | 5850.4067 | 0.001752 | 2.5366 |  | 158.6013 | 5833.4479 | 0.0017873 | 2.5274 |  | 158.0268 | 5812.3175 | 0.0018194 | 2.517 |  | 157.3745 | 5788.3259 | 0.0018488 | 2.5057 |  | 156.6705 | 5762.4343 | 0.0018757 | 2.4939 |  | 155.9342 | 5735.351 | 0.0019005 | 2.4819 |  | 155.1797 | 5707.5995
73 |  | Concrete | 41 | 62.525 |  |  | 2.307 | 28.6071 |  |  | 0.0005504 | 1.4289 |  | 89.3401 | 2555.7643 |  | 6.8537e-05 | 0.20949 |  | 13.0981 | 374.6986 |  | -0.00072972 | 0 |  | 0 | 0 |  | 0.0005504 | 1.4289 |  | 89.3401 | 2555.7643 |  | 0.000763 | 1.8258 |  | 114.1571 | 3265.7052 | 0.00093379 | 2.0821 |  | 130.1814 | 3724.1165 | 0.001074 | 2.2508 |  | 140.7313 | 4025.9183 | 0.0011912 | 2.363 |  | 147.7456 | 4226.5778 | 0.0012905 | 2.4376 |  | 152.409 | 4359.9837 | 0.0013759 | 2.4866 |  | 155.4722 | 4447.6118 | 0.00145 | 2.5178 |  | 157.4256 | 4503.4928 | 0.0015149 | 2.5366 |  | 158.598 | 4537.0316 | 0.0015723 | 2.5464 |  | 159.2146 | 4554.6707 | 0.0016234 | 2.5499 |  | 159.4325 | 4560.9065 | 0.0016691 | 2.5488 |  | 159.3633 | 4558.9268 | 0.0017103 | 2.5444 |  | 159.087 | 4551.0231 | 0.0017476 | 2.5376 |  | 158.6619 | 4538.861 | 0.0017815 | 2.5291 |  | 158.1307 | 4523.6636 | 0.0018125 | 2.5194 |  | 157.5249 | 4506.3358 | 0.001841 | 2.5089 |  | 156.8683 | 4487.5516 | 0.0018672 | 2.4979 |  | 156.1784 | 4467.8154
74 |  | Concrete | 42 | 62.525 |  |  | 1.6479 | 20.4337 |  |  | 0.00044753 | 1.2058 |  | 75.3927 | 1540.5482 |  | -5.9761e-05 | 0 |  | 0 | 0 |  | -0.00090014 | 0 |  | 0 | 0 |  | 0.00044753 | 1.2058 |  | 75.3927 | 1540.5482 |  | 0.00067134 | 1.6653 |  | 104.1204 | 2127.5615 | 0.00085115 | 1.965 |  | 122.8628 | 2510.5368 | 0.00099876 | 2.1649 |  | 135.3618 | 2765.9377 | 0.0011221 | 2.3 |  | 143.8098 | 2938.561 | 0.0012267 | 2.3918 |  | 149.5499 | 3055.8515 | 0.0013166 | 2.454 |  | 153.4357 | 3135.2534 | 0.0013946 | 2.4954 |  | 156.0269 | 3188.2002 | 0.001463 | 2.5222 |  | 157.6997 | 3222.3826 | 0.0015234 | 2.5384 |  | 158.7131 | 3243.0891 | 0.0015771 | 2.547 |  | 159.2483 | 3254.0259 | 0.0016252 | 2.5499 |  | 159.4346 | 3257.833 | 0.0016686 | 2.5488 |  | 159.3653 | 3256.4173 | 0.0017079 | 2.5447 |  | 159.1087 | 3251.1731 | 0.0017436 | 2.5384 |  | 158.7151 | 3243.1306 | 0.0017763 | 2.5305 |  | 158.2221 | 3233.0572 | 0.0018062 | 2.5215 |  | 157.658 | 3221.5292 | 0.0018338 | 2.5117 |  | 157.0439 | 3208.982
75 |  | Concrete | 43 | 62.525 |  |  | 0.98873 | 12.2602 |  |  | 0.00034465 | 0.9625 |  | 60.1806 | 737.826 |  | -0.00018806 | 0 |  | 0 | 0 |  | -0.0010706 | 0 |  | 0 | 0 |  | 0.00034465 | 0.9625 |  | 60.1806 | 737.826 |  | 0.00057969 | 1.4887 |  | 93.08 | 1141.1786 | 0.0007685 | 1.8349 |  | 114.728 | 1406.5882 | 0.00092351 | 2.0682 |  | 129.3158 | 1585.437 | 0.001053 | 2.228 |  | 139.3041 | 1707.8951 | 0.0011629 | 2.3383 |  | 146.2041 | 1792.4906 | 0.0012573 | 2.4147 |  | 150.9789 | 1851.0305 | 0.0013392 | 2.4672 |  | 154.2614 | 1891.2747 | 0.001411 | 2.5027 |  | 156.4786 | 1918.4589 | 0.0014744 | 2.5258 |  | 157.9253 | 1936.1946 | 0.0015308 | 2.5399 |  | 158.8084 | 1947.0221 | 0.0015814 | 2.5474 |  | 159.2762 | 1952.7575 | 0.0016269 | 2.55 |  | 159.4361 | 1954.7184 | 0.0016682 | 2.5489 |  | 159.3671 | 1953.8723 | 0.0017057 | 2.545 |  | 159.1278 | 1950.938 | 0.00174 | 2.5392 |  | 158.7621 | 1946.454 | 0.0017714 | 2.5318 |  | 158.3031 | 1940.8271 | 0.0018004 | 2.5234 |  | 157.7762 | 1934.3668
76 |  | Concrete | 44 | 62.525 |  |  | 0.32958 | 4.0867 |  |  | 0.00024178 | 0.69898 |  | 43.7039 | 178.6063 |  | -0.00031636 | 0 |  | 0 | 0 |  | -0.001241 | 0 |  | 0 | 0 |  | 0.00024178 | 0.69898 |  | 43.7039 | 178.6063 |  | 0.00048803 | 1.2961 |  | 81.0357 | 331.171 | 0.00068586 | 1.6918 |  | 105.7771 | 432.2828 | 0.00084827 | 1.9607 |  | 122.5932 | 501.0056 | 0.00098399 | 2.1468 |  | 134.2284 | 548.5554 | 0.0010991 | 2.277 |  | 142.3716 | 581.8345 | 0.001198 | 2.3687 |  | 148.1016 | 605.2515 | 0.0012838 | 2.4331 |  | 152.1291 | 621.7107 | 0.001359 | 2.478 |  | 154.9347 | 633.1767 | 0.0014254 | 2.5086 |  | 156.8511 | 641.0084 | 0.0014846 | 2.5288 |  | 158.1128 | 646.1646 | 0.0015376 | 2.5412 |  | 158.8881 | 649.333 | 0.0015853 | 2.5478 |  | 159.2994 | 651.0141 | 0.0016285 | 2.55 |  | 159.4372 | 651.5772 | 0.0016678 | 2.5489 |  | 159.3687 | 651.2974 | 0.0017037 | 2.5453 |  | 159.1447 | 650.382 | 0.0017367 | 2.5398 |  | 158.8037 | 648.9883 | 0.001767 | 2.533 |  | 158.3752 | 647.2369
77 |  | Concrete | 45 | 62.525 |  |  | -0.32958 | -4.0867 |  |  | 0.00013891 | 0.41524 |  | 25.9627 | -106.1025 |  | -0.00044466 | 0 |  | 0 | 0 |  | -0.0014114 | 0 |  | 0 | 0 |  | 0.00013891 | 0.41524 |  | 25.9627 | -106.1025 |  | 0.00039638 | 1.0874 |  | 67.9875 | -277.8468 | 0.00060322 | 1.5355 |  | 96.0101 | -392.3675 | 0.00077302 | 1.8424 |  | 115.1941 | -470.7673 | 0.00091492 | 2.0565 |  | 128.5827 | -525.4832 | 0.0010353 | 2.208 |  | 138.0524 | -564.1833 | 0.0011386 | 2.3159 |  | 144.8039 | -591.7748 | 0.0012284 | 2.3931 |  | 149.6299 | -611.4975 | 0.001307 | 2.4481 |  | 153.0679 | -625.5477 | 0.0013765 | 2.4869 |  | 155.4906 | -635.4485 | 0.0014383 | 2.5136 |  | 157.1615 | -642.277 | 0.0014937 | 2.5313 |  | 158.2702 | -646.8081 | 0.0015436 | 2.5423 |  | 158.9552 | -649.6075 | 0.0015888 | 2.5481 |  | 159.3189 | -651.0938 | 0.0016299 | 2.55 |  | 159.4379 | -651.5802 | 0.0016674 | 2.5489 |  | 159.3702 | -651.3033 | 0.0017019 | 2.5455 |  | 159.1599 | -650.4438 | 0.0017336 | 2.5404 |  | 158.8409 | -649.1404
78 |  | Concrete | 46 | 62.525 |  |  | -0.98873 | -12.2602 |  |  | 3.6036e-05 | 0.11126 |  | 6.9568 | -85.2919 |  | -0.00057295 | 0 |  | 0 | 0 |  | -0.0015818 | 0 |  | 0 | 0 |  | 3.6036e-05 | 0.11126 |  | 6.9568 | -85.2919 |  | 0.00030472 | 0.86262 |  | 53.9355 | -661.2603 | 0.00052058 | 1.3663 |  | 85.4269 | -1047.3507 | 0.00069778 | 1.7132 |  | 107.1184 | -1313.2924 | 0.00084586 | 1.9571 |  | 122.3672 | -1500.2454 | 0.00097146 | 2.1311 |  | 133.2466 | -1633.6293 | 0.0010793 | 2.2565 |  | 141.0858 | -1729.7398 | 0.001173 | 2.3473 |  | 146.764 | -1799.3555 | 0.001255 | 2.4131 |  | 150.8783 | -1849.7979 | 0.0013275 | 2.4605 |  | 153.8438 | -1886.155 | 0.0013921 | 2.4943 |  | 155.9545 | -1912.0333 | 0.0014499 | 2.5178 |  | 157.4227 | -1930.0333 | 0.0015019 | 2.5334 |  | 158.4036 | -1942.0588 | 0.0015491 | 2.5432 |  | 159.0123 | -1949.5221 | 0.001592 | 2.5483 |  | 159.3354 | -1953.4833 | 0.0016312 | 2.55 |  | 159.4384 | -1954.7462 | 0.0016671 | 2.5489 |  | 159.3715 | -1953.9262 | 0.0017002 | 2.5458 |  | 159.1735 | -1951.4978
79 |  | Concrete | 47 | 62.525 |  |  | -1.6479 | -20.4337 |  |  | -6.6836e-05 | 0 |  | 0 | 0 |  | -0.00070125 | 0 |  | 0 | 0 |  | -0.0017522 | 0 |  | 0 | 0 |  | -6.6836e-05 | 0 |  | 0 | 0 |  | 0.00021307 | 0.62183 |  | 38.8797 | -794.4552 | 0.00043793 | 1.184 |  | 74.0276 | -1512.6549 | 0.00062254 | 1.5732 |  | 98.3661 | -2009.9803 | 0.0007768 | 1.8486 |  | 115.5816 | -2361.7561 | 0.00090764 | 2.0464 |  | 127.9541 | -2614.5702 | 0.00102 | 2.1903 |  | 136.9473 | -2798.335 | 0.0011176 | 2.2956 |  | 143.5313 | -2932.869 | 0.0012031 | 2.3729 |  | 148.3659 | -3031.6576 | 0.0012786 | 2.4296 |  | 151.9106 | -3104.0901 | 0.0013458 | 2.4709 |  | 154.4919 | -3156.8347 | 0.001406 | 2.5005 |  | 156.3455 | -3194.71 | 0.0014603 | 2.5213 |  | 157.6444 | -3221.2518 | 0.0015094 | 2.5353 |  | 158.5173 | -3239.0891 | 0.0015541 | 2.544 |  | 159.0611 | -3250.2007 | 0.0015949 | 2.5486 |  | 159.3494 | -3256.0911 | 0.0016323 | 2.55 |  | 159.4387 | -3257.9155 | 0.0016668 | 2.5489 |  | 159.3727 | -3256.5682
80 |  | Concrete | 48 | 62.525 |  |  | -2.307 | -28.6071 |  |  | -0.00016971 | 0 |  | 0 | 0 |  | -0.00082955 | 0 |  | 0 | 0 |  | -0.0019226 | 0 |  | 0 | 0 |  | -0.00016971 | 0 |  | 0 | 0 |  | 0.00012142 | 0.36498 |  | 22.8201 | -652.817 | 0.00035529 | 0.9886 |  | 61.8122 | -1768.268 | 0.00054729 | 1.4224 |  | 88.9373 | -2544.2418 | 0.00070774 | 1.7309 |  | 108.2262 | -3096.0403 | 0.00084382 | 1.954 |  | 122.1749 | -3495.0724 | 0.0009607 | 2.1174 |  | 132.3884 | -3787.2518 | 0.0010622 | 2.238 |  | 139.9317 | -4003.0437 | 0.0011511 | 2.3276 |  | 145.5305 | -4163.2107 | 0.0012296 | 2.3941 |  | 149.6911 | -4282.2327 | 0.0012996 | 2.4434 |  | 152.7735 | -4370.4117 | 0.0013622 | 2.4796 |  | 155.0385 | -4435.2059 | 0.0014186 | 2.5058 |  | 156.6777 | -4482.0987 | 0.0014697 | 2.5243 |  | 157.834 | -4515.1764 | 0.0015161 | 2.5368 |  | 158.6151 | -4537.521 | 0.0015586 | 2.5446 |  | 159.1031 | -4551.4823 | 0.0015976 | 2.5488 |  | 159.3613 | -4558.8687 | 0.0016334 | 2.55 |  | 159.4387 | -4561.0843
81 |  | Concrete | 49 | 62.525 |  |  | -2.9662 | -36.7806 |  |  | -0.00027258 | 0 |  | 0 | 0 |  | -0.00095785 | 0 |  | 0 | 0 |  | -0.0020931 | 0 |  | 0 | 0 |  | -0.00027258 | 0 |  | 0 | 0 |  | 2.9761e-05 | 0.092069 |  | 5.7566 | -211.7312 | 0.00027265 | 0.78018 |  | 48.7806 | -1794.1781 | 0.00047205 | 1.2608 |  | 78.832 | -2899.4876 | 0.00063868 | 1.6042 |  | 100.3008 | -3689.1228 | 0.00078001 | 1.8538 |  | 115.909 | -4263.2024 | 0.00090139 | 2.0377 |  | 127.4091 | -4686.1815 | 0.0010068 | 2.1746 |  | 135.9653 | -5000.8851 | 0.0010991 | 2.277 |  | 142.3724 | -5236.5407 | 0.0011807 | 2.354 |  | 147.1853 | -5413.5618 | 0.0012533 | 2.4118 |  | 150.7995 | -5546.4948 | 0.0013183 | 2.455 |  | 153.5018 | -5645.8884 | 0.0013769 | 2.4871 |  | 155.5035 | -5719.5117 | 0.00143 | 2.5104 |  | 156.9623 | -5773.1653 | 0.0014782 | 2.5269 |  | 157.9973 | -5811.2331 | 0.0015223 | 2.5382 |  | 158.6996 | -5837.0642 | 0.0015628 | 2.5452 |  | 159.1394 | -5853.2426 | 0.0016 | 2.5489 |  | 159.3715 | -5861.7788
82 |  | Concrete | 50 | 62.525 |  |  | -3.6253 | -44.9541 |  |  | -0.00037545 | 0 |  | 0 | 0 |  | -0.0010861 | 0 |  | 0 | 0 |  | -0.0022635 | 0 |  | 0 | 0 |  | -0.00037545 | 0 |  | 0 | 0 |  | -6.1893e-05 | 0 |  | 0 | 0 | 0.00019001 | 0.5587 |  | 34.9329 | -1570.3733 | 0.0003968 | 1.0884 |  | 68.0501 | -3059.1284 | 0.00056962 | 1.4683 |  | 91.8055 | -4127.0286 | 0.00071619 | 1.7458 |  | 109.1565 | -4907.0268 | 0.00084207 | 1.9514 |  | 122.0094 | -5484.8155 | 0.00095136 | 2.1053 |  | 131.6322 | -5917.3989 | 0.0010471 | 2.2214 |  | 138.8914 | -6243.7313 | 0.0011317 | 2.3094 |  | 144.3931 | -6491.0563 | 0.001207 | 2.3762 |  | 148.5698 | -6678.8144 | 0.0012745 | 2.4268 |  | 151.7355 | -6821.125 | 0.0013352 | 2.465 |  | 154.1219 | -6928.4029 | 0.0013903 | 2.4934 |  | 155.9022 | -7008.4374 | 0.0014403 | 2.5143 |  | 157.2077 | -7067.1255 | 0.0014861 | 2.5292 |  | 158.1388 | -7108.9813 | 0.001528 | 2.5394 |  | 158.7731 | -7137.4939 | 0.0015666 | 2.5457 |  | 159.1711 | -7155.3845
83 |  | Concrete | 51 | 62.525 |  |  | -4.2845 | -53.1275 |  |  | -0.00047833 | 0 |  | 0 | 0 |  | -0.0012144 | 0 |  | 0 | 0 |  | -0.0024339 | 0 |  | 0 | 0 |  | -0.00047833 | 0 |  | 0 | 0 |  | -0.00015355 | 0 |  | 0 | 0 | 0.00010736 | 0.32417 |  | 20.269 | -1076.8415 | 0.00032156 | 0.9051 |  | 56.5917 | -3006.5749 | 0.00050055 | 1.3233 |  | 82.7402 | -4395.7825 | 0.00065237 | 1.63 |  | 101.9173 | -5414.6122 | 0.00078276 | 1.8583 |  | 116.1892 | -6172.8453 | 0.00089595 | 2.0301 |  | 126.9322 | -6743.5908 | 0.00099515 | 2.1605 |  | 135.0876 | -7176.8664 | 0.0010828 | 2.2601 |  | 141.3146 | -7507.6952 | 0.0011608 | 2.3364 |  | 146.0844 | -7761.1012 | 0.0012306 | 2.3949 |  | 149.7394 | -7955.2832 | 0.0012936 | 2.4395 |  | 152.5327 | -8103.6845 | 0.0013506 | 2.4735 |  | 154.6538 | -8216.3741 | 0.0014024 | 2.4989 |  | 156.2465 | -8300.9871 | 0.0014498 | 2.5177 |  | 157.4208 | -8363.3778 | 0.0014932 | 2.5312 |  | 158.2622 | -8408.0794 | 0.0015332 | 2.5404 |  | 158.8373 | -8438.6341
84 |  | Concrete | 52 | 62.525 |  |  | -4.9436 | -61.301 |  |  | -0.0005812 | 0 |  | 0 | 0 |  | -0.0013427 | 0 |  | 0 | 0 |  | -0.0026043 | 0 |  | 0 | 0 |  | -0.0005812 | 0 |  | 0 | 0 |  | -0.0002452 | 0 |  | 0 | 0 | 2.472e-05 | 0.076593 |  | 4.789 | -293.5708 | 0.00024631 | 0.71102 |  | 44.4567 | -2725.2378 | 0.00043149 | 1.1692 |  | 73.105 | -4481.4094 | 0.00058855 | 1.5065 |  | 94.1914 | -5774.0251 | 0.00072344 | 1.7585 |  | 109.9487 | -6739.9622 | 0.00084055 | 1.9491 |  | 121.8654 | -7470.4665 | 0.00094317 | 2.0945 |  | 130.9609 | -8028.0295 | 0.0010338 | 2.2063 |  | 137.9498 | -8456.4573 | 0.0011145 | 2.2926 |  | 143.3433 | -8787.0854 | 0.0011868 | 2.3593 |  | 147.5136 | -9042.7305 | 0.0012519 | 2.4108 |  | 150.7361 | -9240.2686 | 0.0013109 | 2.4505 |  | 153.2171 | -9392.3568 | 0.0013645 | 2.4808 |  | 155.1134 | -9508.6065 | 0.0014135 | 2.5037 |  | 156.5456 | -9596.3981 | 0.0014585 | 2.5207 |  | 157.6069 | -9661.4561 | 0.0014998 | 2.5329 |  | 158.3704 | -9708.2604
85 |  | Concrete | 53 | 62.525 |  |  | -5.6028 | -69.4744 |  |  | -0.00068407 | 0 |  | 0 | 0 |  | -0.001471 | 0 |  | 0 | 0 |  | -0.0027747 | 0 |  | 0 | 0 |  | -0.00068407 | 0 |  | 0 | 0 |  | -0.00033686 | 0 |  | 0 | 0 | -5.7922e-05 | 0 |  | 0 | 0 | 0.00017107 | 0.50612 |  | 31.6451 | -2198.5278 | 0.00036243 | 1.006 |  | 62.8999 | -4369.9342 | 0.00052473 | 1.3751 |  | 85.9788 | -5973.3319 | 0.00066413 | 1.6519 |  | 103.2877 | -7175.8576 | 0.00078515 | 1.8622 |  | 116.4318 | -8089.0315 | 0.00089119 | 2.0234 |  | 126.5113 | -8789.3044 | 0.00098489 | 2.1479 |  | 134.2986 | -9330.3217 | 0.0010683 | 2.2446 |  | 140.3465 | -9750.4977 | 0.001143 | 2.32 |  | 145.0581 | -10077.8345 | 0.0012102 | 2.3788 |  | 148.7319 | -10333.0674 | 0.0012712 | 2.4245 |  | 151.592 | -10531.7671 | 0.0013266 | 2.46 |  | 153.8087 | -10685.7724 | 0.0013772 | 2.4872 |  | 155.5131 | -10804.1867 | 0.0014237 | 2.5079 |  | 156.807 | -10894.0806 | 0.0014664 | 2.5233 |  | 157.7702 | -10960.9961
86 |  | Concrete | 54 | 62.525 |  |  | -6.2619 | -77.6479 |  |  | -0.00078694 | 0 |  | 0 | 0 |  | -0.0015993 | 0 |  | 0 | 0 |  | -0.0029452 | 0 |  | 0 | 0 |  | -0.00078694 | 0 |  | 0 | 0 |  | -0.00042851 | 0 |  | 0 | 0 | -0.00014056 | 0 |  | 0 | 0 | 9.5826e-05 | 0.2904 |  | 18.157 | -1409.8556 | 0.00029337 | 0.83366 |  | 52.1248 | -4047.3819 | 0.00046092 | 1.236 |  | 77.2796 | -6000.5993 | 0.00060481 | 1.5387 |  | 96.2064 | -7470.2229 | 0.00072974 | 1.7694 |  | 110.6313 | -8590.2916 | 0.00083922 | 1.947 |  | 121.7389 | -9452.7748 | 0.00093594 | 2.0849 |  | 130.3611 | -10122.2672 | 0.001022 | 2.1926 |  | 137.0941 | -10645.0685 | 0.0010991 | 2.2771 |  | 142.373 | -11054.9626 | 0.0011686 | 2.3434 |  | 146.5203 | -11376.9931 | 0.0012315 | 2.3955 |  | 149.7785 | -11629.9863 | 0.0012887 | 2.4363 |  | 152.3322 | -11828.2735 | 0.001341 | 2.4682 |  | 154.3234 | -11982.8878 | 0.0013889 | 2.4928 |  | 155.8627 | -12102.4098 | 0.0014331 | 2.5116 |  | 157.0367 | -12193.574
87 |  | Concrete | 55 | 62.525 |  |  | -6.9211 | -85.8214 |  |  | -0.00088982 | 0 |  | 0 | 0 |  | -0.0017276 | 0 |  | 0 | 0 |  | -0.0031156 | 0 |  | 0 | 0 |  | -0.00088982 | 0 |  | 0 | 0 |  | -0.00052017 | 0 |  | 0 | 0 | -0.00022321 | 0 |  | 0 | 0 | 2.0582e-05 | 0.063853 |  | 3.9924 | -342.632 | 0.00022431 | 0.65222 |  | 40.7798 | -3499.7772 | 0.0003971 | 1.0891 |  | 68.0937 | -5843.8937 | 0.0005455 | 1.4187 |  | 88.7046 | -7612.7495 | 0.00067434 | 1.6708 |  | 104.4641 | -8965.2524 | 0.00078724 | 1.8656 |  | 116.6437 | -10010.5244 | 0.00088699 | 2.0174 |  | 126.1373 | -10825.2729 | 0.00097576 | 2.1365 |  | 133.5859 | -11464.5282 | 0.0010553 | 2.2304 |  | 139.4581 | -11968.4824 | 0.0011269 | 2.3047 |  | 144.1011 | -12366.9578 | 0.0011918 | 2.3635 |  | 147.7767 | -12682.396 | 0.0012508 | 2.41 |  | 150.6839 | -12931.8986 | 0.0013047 | 2.4466 |  | 152.9764 | -13128.6459 | 0.0013541 | 2.4754 |  | 154.7738 | -13282.9004 | 0.0013997 | 2.4977 |  | 156.17 | -13402.7269
88 |  | Concrete | 56 | 62.525 |  |  | -7.5802 | -93.9948 |  |  | -0.00099269 | 0 |  | 0 | 0 |  | -0.0018559 | 0 |  | 0 | 0 |  | -0.003286 | 0 |  | 0 | 0 |  | -0.00099269 | 0 |  | 0 | 0 |  | -0.00061182 | 0 |  | 0 | 0 | -0.00030585 | 0 |  | 0 | 0 | -5.4662e-05 | 0 |  | 0 | 0 | 0.00015525 | 0.46165 |  | 28.8648 | -2713.145 | 0.00033328 | 0.93436 |  | 58.4211 | -5491.2818 | 0.00048619 | 1.292 |  | 80.7824 | -7593.1288 | 0.00061893 | 1.5663 |  | 97.93 | -9204.9194 | 0.00073526 | 1.7789 |  | 111.2256 | -10454.6369 | 0.00083804 | 1.9453 |  | 121.6271 | -11432.3176 | 0.0009295 | 2.0763 |  | 129.8221 | -12202.6074 | 0.0010114 | 2.1801 |  | 136.3135 | -12812.7614 | 0.0010852 | 2.2627 |  | 141.4745 | -13297.8736 | 0.0011521 | 2.3285 |  | 145.5865 | -13684.3776 | 0.0012129 | 2.3809 |  | 148.8639 | -13992.4363 | 0.0012684 | 2.4226 |  | 151.4722 | -14237.6053 | 0.0013194 | 2.4557 |  | 153.5404 | -14432.0094 | 0.0013663 | 2.4817 |  | 155.1701 | -14585.1875
89 |  | Concrete | 57 | 62.525 |  |  | -8.2394 | -102.1683 |  |  | -0.0010956 | 0 |  | 0 | 0 |  | -0.0019842 | 0 |  | 0 | 0 |  | -0.0034564 | 0 |  | 0 | 0 |  | -0.0010956 | 0 |  | 0 | 0 |  | -0.00070348 | 0 |  | 0 | 0 | -0.00038849 | 0 |  | 0 | 0 | -0.00012991 | 0 |  | 0 | 0 | 8.6185e-05 | 0.26197 |  | 16.3799 | -1673.5104 | 0.00026946 | 0.77188 |  | 48.2618 | -4930.83 | 0.00042687 | 1.1586 |  | 72.4398 | -7401.0522 | 0.00056353 | 1.4559 |  | 91.0292 | -9300.2985 | 0.00068328 | 1.6871 |  | 105.4847 | -10777.196 | 0.00078909 | 1.8685 |  | 116.8306 | -11936.3803 | 0.00088325 | 2.012 |  | 125.8026 | -12853.0366 | 0.00096758 | 2.1262 |  | 132.9391 | -13582.167 | 0.0010436 | 2.2174 |  | 138.6404 | -14164.6528 | 0.0011124 | 2.2904 |  | 143.2079 | -14631.3126 | 0.0011749 | 2.349 |  | 146.8721 | -15005.6754 | 0.0012321 | 2.396 |  | 149.8107 | -15305.9104 | 0.0012846 | 2.4336 |  | 152.1626 | -15546.1935 | 0.0013329 | 2.4636 |  | 154.0369 | -15737.6886
90 |  | Concrete | 58 | 62.525 |  |  | -8.8985 | -110.3418 |  |  | -0.0011984 | 0 |  | 0 | 0 |  | -0.0021125 | 0 |  | 0 | 0 |  | -0.0036268 | 0 |  | 0 | 0 |  | -0.0011984 | 0 |  | 0 | 0 |  | -0.00079513 | 0 |  | 0 | 0 | -0.00047114 | 0 |  | 0 | 0 | -0.00020515 | 0 |  | 0 | 0 | 1.7124e-05 | 0.05318 |  | 3.3251 | -366.8981 | 0.00020564 | 0.60161 |  | 37.6159 | -4150.6049 | 0.00036756 | 1.0184 |  | 63.6768 | -7026.2111 | 0.00050812 | 1.3396 |  | 83.7615 | -9242.3952 | 0.0006313 | 1.5901 |  | 99.421 | -10970.2854 | 0.00074014 | 1.7872 |  | 111.7477 | -12330.44 | 0.00083699 | 1.9437 |  | 121.5274 | -13409.5462 | 0.00092374 | 2.0685 |  | 129.3351 | -14271.0668 | 0.0010019 | 2.1687 |  | 135.5988 | -14962.2074 | 0.0010727 | 2.2494 |  | 140.6411 | -15518.5825 | 0.001137 | 2.3144 |  | 144.7086 | -15967.4045 | 0.0011959 | 2.3669 |  | 147.9921 | -16329.7055 | 0.0012498 | 2.4093 |  | 150.6402 | -16621.9095 | 0.0012995 | 2.4434 |  | 152.7705 | -16856.9628
91 |  | Concrete | 59 | 62.525 |  |  | -9.5577 | -118.5152 |  |  | -0.0013013 | 0 |  | 0 | 0 |  | -0.0022408 | 0 |  | 0 | 0 |  | -0.0037973 | 0 |  | 0 | 0 |  | -0.0013013 | 0 |  | 0 | 0 |  | -0.00088678 | 0 |  | 0 | 0 | -0.00055378 | 0 |  | 0 | 0 | -0.00028039 | 0 |  | 0 | 0 | -5.1938e-05 | 0 |  | 0 | 0 | 0.00014183 | 0.42356 |  | 26.4833 | -3138.673 | 0.00030824 | 0.87155 |  | 54.4934 | -6458.2969 | 0.00045272 | 1.2175 |  | 76.1271 | -9022.2152 | 0.00057933 | 1.488 |  | 93.0344 | -11025.9888 | 0.00069119 | 1.7014 |  | 106.3785 | -12607.4756 | 0.00079073 | 1.8712 |  | 116.9965 | -13865.8667 | 0.0008799 | 2.0072 |  | 125.5014 | -14873.8283 | 0.00096022 | 2.1167 |  | 132.3496 | -15685.4497 | 0.001033 | 2.2053 |  | 137.8858 | -16341.5686 | 0.0010991 | 2.2771 |  | 142.3734 | -16873.4124 | 0.0011596 | 2.3353 |  | 146.0161 | -17305.1351 | 0.001215 | 2.3826 |  | 148.9734 | -17655.6143 | 0.0012661 | 2.421 |  | 151.3708 | -17939.743
92 |  | Concrete | 60 | 62.525 |  |  | -10.2168 | -126.6887 |  |  | -0.0014042 | 0 |  | 0 | 0 |  | -0.0023691 | 0 |  | 0 | 0 |  | -0.0039677 | 0 |  | 0 | 0 |  | -0.0014042 | 0 |  | 0 | 0 |  | -0.00097844 | 0 |  | 0 | 0 | -0.00063642 | 0 |  | 0 | 0 | -0.00035564 | 0 |  | 0 | 0 | -0.000121 | 0 |  | 0 | 0 | 7.8008e-05 | 0.23773 |  | 14.864 | -1883.1008 | 0.00024893 | 0.71795 |  | 44.8896 | -5687.001 | 0.00039731 | 1.0896 |  | 68.1258 | -8630.7641 | 0.00052735 | 1.3806 |  | 86.3249 | -10936.3899 | 0.00064224 | 1.6109 |  | 100.723 | -12760.466 | 0.00074448 | 1.7946 |  | 112.2099 | -14215.7286 | 0.00083605 | 1.9422 |  | 121.438 | -15384.819 | 0.00091855 | 2.0615 |  | 128.893 | -16329.2918 | 0.00099325 | 2.1582 |  | 134.9422 | -17095.6525 | 0.0010612 | 2.237 |  | 139.8664 | -17719.4877 | 0.0011233 | 2.3012 |  | 143.8829 | -18228.3435 | 0.0011803 | 2.3537 |  | 147.162 | -18643.7645 | 0.0012327 | 2.3964 |  | 149.8378 | -18982.762
93 |  | Concrete | 61 | 62.525 |  |  | -10.876 | -134.8622 |  |  | -0.0015071 | 0 |  | 0 | 0 |  | -0.0024974 | 0 |  | 0 | 0 |  | -0.0041381 | 0 |  | 0 | 0 |  | -0.0015071 | 0 |  | 0 | 0 |  | -0.0010701 | 0 |  | 0 | 0 | -0.00071906 | 0 |  | 0 | 0 | -0.00043088 | 0 |  | 0 | 0 | -0.00019006 | 0 |  | 0 | 0 | 1.4191e-05 | 0.044111 |  | 2.758 | -371.955 | 0.00018961 | 0.55762 |  | 34.8653 | -4702.0147 | 0.00034191 | 0.95574 |  | 59.7577 | -8059.0476 | 0.00047537 | 1.2682 |  | 79.2926 | -10693.5724 | 0.00059328 | 1.5159 |  | 94.7811 | -12782.3902 | 0.00069822 | 1.714 |  | 107.1677 | -14452.8624 | 0.00079221 | 1.8736 |  | 117.1448 | -15798.4064 | 0.00087688 | 2.0029 |  | 125.2289 | -16888.6458 | 0.00095355 | 2.1081 |  | 131.8103 | -17776.2156 | 0.0010233 | 2.1941 |  | 137.1876 | -18501.4193 | 0.001087 | 2.2646 |  | 141.5925 | -19095.475 | 0.0011455 | 2.3224 |  | 145.2062 | -19582.8172 | 0.0011993 | 2.3698 |  | 148.1717 | -19982.7524
94 |  | Concrete | 62 | 62.525 |  |  | -11.5351 | -143.0356 |  |  | -0.0016099 | 0 |  | 0 | 0 |  | -0.0026257 | 0 |  | 0 | 0 |  | -0.0043085 | 0 |  | 0 | 0 |  | -0.0016099 | 0 |  | 0 | 0 |  | -0.0011617 | 0 |  | 0 | 0 | -0.00080171 | 0 |  | 0 | 0 | -0.00050613 | 0 |  | 0 | 0 | -0.00025912 | 0 |  | 0 | 0 | -4.9627e-05 | 0 |  | 0 | 0 | 0.0001303 | 0.39057 |  | 24.4207 | -3493.0296 | 0.00028651 | 0.81604 |  | 51.0228 | -7298.0713 | 0.00042339 | 1.1505 |  | 71.9375 | -10289.6201 | 0.00054433 | 1.4163 |  | 88.553 | -12666.2271 | 0.00065196 | 1.6293 |  | 101.8697 | -14570.9985 | 0.00074836 | 1.8012 |  | 112.622 | -16108.958 | 0.00083521 | 1.9409 |  | 121.3573 | -17358.4239 | 0.00091384 | 2.055 |  | 128.4899 | -18378.6394 | 0.00098539 | 2.1485 |  | 134.3371 | -19214.9957 | 0.0010508 | 2.2254 |  | 139.1449 | -19902.6741 | 0.0011107 | 2.2888 |  | 143.1058 | -20469.229 | 0.0011659 | 2.341 |  | 146.3723 | -20936.447
95 |  | Concrete | 63 | 62.525 |  |  | -12.1943 | -151.2091 |  |  | -0.0017128 | 0 |  | 0 | 0 |  | -0.002754 | 0 |  | 0 | 0 |  | -0.0044789 | 0 |  | 0 | 0 |  | -0.0017128 | 0 |  | 0 | 0 |  | -0.0012534 | 0 |  | 0 | 0 | -0.00088435 | 0 |  | 0 | 0 | -0.00058137 | 0 |  | 0 | 0 | -0.00032818 | 0 |  | 0 | 0 | -0.00011345 | 0 |  | 0 | 0 | 7.0986e-05 | 0.2168 |  | 13.5556 | -2049.7368 | 0.0002311 | 0.67047 |  | 41.921 | -6338.8409 | 0.00037141 | 1.0277 |  | 64.2595 | -9716.6165 | 0.00049538 | 1.3121 |  | 82.0384 | -12404.9557 | 0.00060571 | 1.5404 |  | 96.3161 | -14563.8675 | 0.00070452 | 1.7252 |  | 107.8694 | -16310.8413 | 0.00079354 | 1.8757 |  | 117.2783 | -17733.5382 | 0.00087414 | 1.9989 |  | 124.9813 | -18898.3054 | 0.00094748 | 2.1002 |  | 131.3149 | -19856.0057 | 0.0010145 | 2.1838 |  | 136.54 | -20646.0851 | 0.0010759 | 2.2529 |  | 140.861 | -21299.4567 | 0.0011325 | 2.3101 |  | 144.4396 | -21840.5786
96 |  | Concrete | 64 | 62.525 |  |  | -12.8534 | -159.3826 |  |  | -0.0018157 | 0 |  | 0 | 0 |  | -0.0028823 | 0 |  | 0 | 0 |  | -0.0046494 | 0 |  | 0 | 0 |  | -0.0018157 | 0 |  | 0 | 0 |  | -0.0013451 | 0 |  | 0 | 0 | -0.00096699 | 0 |  | 0 | 0 | -0.00065662 | 0 |  | 0 | 0 | -0.00039725 | 0 |  | 0 | 0 | -0.00017726 | 0 |  | 0 | 0 | 1.1671e-05 | 0.036308 |  | 2.2702 | -361.828 | 0.0001757 | 0.51903 |  | 32.4525 | -5172.3621 | 0.00031944 | 0.89978 |  | 56.2586 | -8966.6455 | 0.00044643 | 1.2033 |  | 75.2376 | -11991.5548 | 0.00055945 | 1.4475 |  | 90.5068 | -14425.1998 | 0.00066068 | 1.6455 |  | 102.8872 | -16398.4239 | 0.00075187 | 1.8071 |  | 112.9917 | -18008.901 | 0.00083444 | 1.9398 |  | 121.2843 | -19330.595 | 0.00090957 | 2.0491 |  | 128.1209 | -20420.2381 | 0.00097821 | 2.1396 |  | 133.7778 | -21321.8524 | 0.0010412 | 2.2147 |  | 138.4716 | -22069.9572 | 0.0010991 | 2.2771 |  | 142.3737 | -22691.88
97 |  | Concrete | 65 | 32 |  |  | -13.3438 | -165.4628 |  |  | -0.0018922 | 0 |  | 0 | 0 |  | -0.0029778 | 0 |  | 0 | 0 |  | -0.0047761 | 0 |  | 0 | 0 |  | -0.0018922 | 0 |  | 0 | 0 |  | -0.0014132 | 0 |  | 0 | 0 | -0.0010285 | 0 |  | 0 | 0 | -0.00071259 | 0 |  | 0 | 0 | -0.00044862 | 0 |  | 0 | 0 | -0.00022474 | 0 |  | 0 | 0 | -3.2453e-05 | 0 |  | 0 | 0 | 0.00013448 | 0.40257 |  | 12.8823 | -2131.5498 | 0.00028077 | 0.80124 |  | 25.6396 | -4242.4013 | 0.00041002 | 1.1194 |  | 35.8219 | -5927.194 | 0.00052504 | 1.3758 |  | 44.0243 | -7284.3844 | 0.00062806 | 1.5839 |  | 50.6841 | -8386.3258 | 0.00072087 | 1.754 |  | 56.1277 | -9287.0485 | 0.00080491 | 1.8938 |  | 60.6026 | -10027.482 | 0.00088136 | 2.0093 |  | 64.2986 | -10639.0324 | 0.00095122 | 2.1051 |  | 67.363 | -11146.0788 | 0.0010153 | 2.1847 |  | 69.9115 | -11567.7456 | 0.0010743 | 2.2511 |  | 72.0354 | -11919.1791
98 |  | Concrete | 66 | 32 |  |  | -13.6653 | -169.4499 |  |  | -0.0019424 | 0 |  | 0 | 0 |  | -0.0030404 | 0 |  | 0 | 0 |  | -0.0048593 | 0 |  | 0 | 0 |  | -0.0019424 | 0 |  | 0 | 0 |  | -0.0014579 | 0 |  | 0 | 0 | -0.0010688 | 0 |  | 0 | 0 | -0.00074929 | 0 |  | 0 | 0 | -0.00048231 | 0 |  | 0 | 0 | -0.00025587 | 0 |  | 0 | 0 | -6.1386e-05 | 0 |  | 0 | 0 | 0.00010746 | 0.32444 |  | 10.3822 | -1759.2663 | 0.00025541 | 0.73507 |  | 23.5222 | -3985.8387 | 0.00038614 | 1.0631 |  | 34.0177 | -5764.2906 | 0.00050248 | 1.3275 |  | 42.479 | -7198.0601 | 0.00060667 | 1.5423 |  | 49.3549 | -8363.1777 | 0.00070054 | 1.7181 |  | 54.9805 | -9316.4324 | 0.00078554 | 1.8628 |  | 59.6097 | -10100.8534 | 0.00086287 | 1.9824 |  | 63.4374 | -10749.4658 | 0.00093353 | 2.0817 |  | 66.6151 | -11287.9119 | 0.00099834 | 2.1644 |  | 69.2613 | -11736.3119 | 0.001058 | 2.2334 |  | 71.4701 | -12110.6048
99 |  | Concrete | 67 | 32 |  |  | -13.9868 | -173.4369 |  |  | -0.0019926 | 0 |  | 0 | 0 |  | -0.0031029 | 0 |  | 0 | 0 |  | -0.0049424 | 0 |  | 0 | 0 |  | -0.0019926 | 0 |  | 0 | 0 |  | -0.0015027 | 0 |  | 0 | 0 | -0.0011091 | 0 |  | 0 | 0 | -0.000786 | 0 |  | 0 | 0 | -0.000516 | 0 |  | 0 | 0 | -0.000287 | 0 |  | 0 | 0 | -9.032e-05 | 0 |  | 0 | 0 | 8.0429e-05 | 0.24492 |  | 7.8374 | -1359.2989 | 0.00023006 | 0.66767 |  | 21.3655 | -3705.5729 | 0.00036226 | 1.0056 |  | 32.1786 | -5580.9522 | 0.00047991 | 1.2782 |  | 40.9026 | -7094.0129 | 0.00058529 | 1.4999 |  | 47.9977 | -8324.5788 | 0.00068021 | 1.6815 |  | 53.8079 | -9332.2854 | 0.00076617 | 1.8311 |  | 58.5938 | -10162.3286 | 0.00084438 | 1.9549 |  | 62.5553 | -10849.4044 | 0.00091583 | 2.0577 |  | 65.8479 | -11420.4591 | 0.00098137 | 2.1435 |  | 68.5935 | -11896.6413 | 0.0010417 | 2.2153 |  | 70.8886 | -12294.7087
100 |  | Concrete | 68 | 32 |  |  | -14.3084 | -177.424 |  |  | -0.0020427 | 0 |  | 0 | 0 |  | -0.0031655 | 0 |  | 0 | 0 |  | -0.0050255 | 0 |  | 0 | 0 |  | -0.0020427 | 0 |  | 0 | 0 |  | -0.0015474 | 0 |  | 0 | 0 | -0.0011494 | 0 |  | 0 | 0 | -0.0008227 | 0 |  | 0 | 0 | -0.00054969 | 0 |  | 0 | 0 | -0.00031813 | 0 |  | 0 | 0 | -0.00011925 | 0 |  | 0 | 0 | 5.3403e-05 | 0.164 |  | 5.248 | -931.1132 | 0.0002047 | 0.59905 |  | 19.1695 | -3401.1336 | 0.00033838 | 0.94702 |  | 30.3046 | -5376.7617 | 0.00045735 | 1.228 |  | 39.295 | -6971.8703 | 0.0005639 | 1.4566 |  | 46.6126 | -8270.1946 | 0.00065989 | 1.6441 |  | 52.6102 | -9334.3052 | 0.00074681 | 1.7986 |  | 57.555 | -10211.6331 | 0.00082588 | 1.9266 |  | 61.6523 | -10938.5981 | 0.00089814 | 2.0332 |  | 65.0616 | -11543.4916 | 0.00096441 | 2.1221 |  | 67.9081 | -12048.5234 | 0.0010254 | 2.1966 |  | 70.2909 | -12471.2967
101 |  | Concrete | 69 | 27.45 |  |  | -52.224 | -172.3598 |  |  | -0.001979 | 0 |  | 0 | 0 |  | -0.003086 | 0 |  | 0 | 0 |  | -0.0049199 | 0 |  | 0 | 0 |  | -0.001979 | 0 |  | 0 | 0 |  | -0.0014906 | 0 |  | 0 | 0 | -0.0010982 | 0 |  | 0 | 0 | -0.00077608 | 0 |  | 0 | 0 | -0.0005069 | 0 |  | 0 | 0 | -0.00027859 | 0 |  | 0 | 0 | -8.2503e-05 | 0 |  | 0 | 0 | 8.7731e-05 | 0.26654 |  | 7.3166 | -1261.0824 | 0.00023691 | 0.686 |  | 18.8308 | -3245.6652 | 0.00036871 | 1.0212 |  | 28.0323 | -4831.6474 | 0.00048601 | 1.2916 |  | 35.4547 | -6110.9627 | 0.00059106 | 1.5115 |  | 41.4899 | -7151.1959 | 0.00068571 | 1.6915 |  | 46.431 | -8002.8362 | 0.00077141 | 1.8397 |  | 50.4999 | -8704.1452 | 0.00084937 | 1.9624 |  | 53.8669 | -9284.4939 | 0.00092061 | 2.0643 |  | 56.6646 | -9766.6915 | 0.00098596 | 2.1492 |  | 58.9966 | -10168.6385 | 0.0010461 | 2.2202 |  | 60.9453 | -10504.5179
102 |  | Concrete | 70 | 27.45 |  |  | -48.6357 | -172.6492 |  |  | -0.0019826 | 0 |  | 0 | 0 |  | -0.0030906 | 0 |  | 0 | 0 |  | -0.004926 | 0 |  | 0 | 0 |  | -0.0019826 | 0 |  | 0 | 0 |  | -0.0014938 | 0 |  | 0 | 0 | -0.0011011 | 0 |  | 0 | 0 | -0.00077875 | 0 |  | 0 | 0 | -0.00050934 | 0 |  | 0 | 0 | -0.00028085 | 0 |  | 0 | 0 | -8.4603e-05 | 0 |  | 0 | 0 | 8.5769e-05 | 0.26074 |  | 7.1574 | -1235.7173 | 0.00023507 | 0.68109 |  | 18.6958 | -3227.8192 | 0.00036698 | 1.017 |  | 27.9173 | -4819.8907 | 0.00048437 | 1.288 |  | 35.356 | -6104.188 | 0.00058951 | 1.5084 |  | 41.405 | -7148.5341 | 0.00068423 | 1.6888 |  | 46.3576 | -8003.5966 | 0.00077 | 1.8374 |  | 50.4362 | -8707.7734 | 0.00084803 | 1.9604 |  | 53.8117 | -9290.5403 | 0.00091933 | 2.0625 |  | 56.6165 | -9774.7883 | 0.00098473 | 2.1477 |  | 58.9547 | -10178.4825 | 0.0010449 | 2.2189 |  | 60.9088 | -10515.8574
103 |  | Concrete | 71 | 27.45 |  |  | -45.0473 | -172.9385 |  |  | -0.0019863 | 0 |  | 0 | 0 |  | -0.0030951 | 0 |  | 0 | 0 |  | -0.004932 | 0 |  | 0 | 0 |  | -0.0019863 | 0 |  | 0 | 0 |  | -0.0014971 | 0 |  | 0 | 0 | -0.0011041 | 0 |  | 0 | 0 | -0.00078141 | 0 |  | 0 | 0 | -0.00051179 | 0 |  | 0 | 0 | -0.00028311 | 0 |  | 0 | 0 | -8.6703e-05 | 0 |  | 0 | 0 | 8.3807e-05 | 0.25494 |  | 6.998 | -1210.2251 | 0.00023323 | 0.67616 |  | 18.5607 | -3209.8644 | 0.00036525 | 1.0128 |  | 27.802 | -4808.0402 | 0.00048273 | 1.2844 |  | 35.2572 | -6097.3319 | 0.00058796 | 1.5053 |  | 41.3199 | -7145.8012 | 0.00068275 | 1.6861 |  | 46.284 | -8004.2948 | 0.00076859 | 1.8351 |  | 50.3725 | -8711.3468 | 0.00084669 | 1.9583 |  | 53.7563 | -9296.5383 | 0.00091804 | 2.0608 |  | 56.5683 | -9782.8423 | 0.00098349 | 2.1462 |  | 58.9128 | -10188.2886 | 0.0010437 | 2.2176 |  | 60.8723 | -10527.1632
104 |  | Concrete | 72 | 27.45 |  |  | -41.4589 | -173.2279 |  |  | -0.0019899 | 0 |  | 0 | 0 |  | -0.0030997 | 0 |  | 0 | 0 |  | -0.004938 | 0 |  | 0 | 0 |  | -0.0019899 | 0 |  | 0 | 0 |  | -0.0015003 | 0 |  | 0 | 0 | -0.001107 | 0 |  | 0 | 0 | -0.00078408 | 0 |  | 0 | 0 | -0.00051423 | 0 |  | 0 | 0 | -0.00028537 | 0 |  | 0 | 0 | -8.8803e-05 | 0 |  | 0 | 0 | 8.1846e-05 | 0.24912 |  | 6.8384 | -1184.6057 | 0.00023139 | 0.67124 |  | 18.4254 | -3191.8007 | 0.00036351 | 1.0086 |  | 27.6866 | -4796.0957 | 0.00048109 | 1.2808 |  | 35.1583 | -6090.3943 | 0.00058641 | 1.5022 |  | 41.2347 | -7142.9972 | 0.00068128 | 1.6834 |  | 46.2104 | -8004.9306 | 0.00076719 | 1.8327 |  | 50.3087 | -8714.8654 | 0.00084535 | 1.9563 |  | 53.7009 | -9302.488 | 0.00091676 | 2.059 |  | 56.5201 | -9790.8535 | 0.00098226 | 2.1447 |  | 58.8707 | -10198.0566 | 0.0010426 | 2.2162 |  | 60.8357 | -10538.4351
105 |  | Concrete | 73 | 27.45 |  |  | -37.8706 | -173.5173 |  |  | -0.0019936 | 0 |  | 0 | 0 |  | -0.0031042 | 0 |  | 0 | 0 |  | -0.0049441 | 0 |  | 0 | 0 |  | -0.0019936 | 0 |  | 0 | 0 |  | -0.0015036 | 0 |  | 0 | 0 | -0.0011099 | 0 |  | 0 | 0 | -0.00078674 | 0 |  | 0 | 0 | -0.00051668 | 0 |  | 0 | 0 | -0.00028763 | 0 |  | 0 | 0 | -9.0903e-05 | 0 |  | 0 | 0 | 7.9884e-05 | 0.2433 |  | 6.6786 | -1158.8589 | 0.00022955 | 0.6663 |  | 18.29 | -3173.6278 | 0.00036178 | 1.0044 |  | 27.5711 | -4784.0571 | 0.00047946 | 1.2772 |  | 35.0592 | -6083.375 | 0.00058486 | 1.4991 |  | 41.1493 | -7140.1219 | 0.0006798 | 1.6808 |  | 46.1366 | -8005.5041 | 0.00076578 | 1.8304 |  | 50.2447 | -8718.3291 | 0.00084401 | 1.9543 |  | 53.6453 | -9308.3891 | 0.00091548 | 2.0573 |  | 56.4717 | -9798.8217 | 0.00098103 | 2.1431 |  | 58.8286 | -10207.7865 | 0.0010414 | 2.2149 |  | 60.799 | -10549.6731
106 |  | Concrete | 74 | 27.45 |  |  | -34.2822 | -173.8067 |  |  | -0.0019972 | 0 |  | 0 | 0 |  | -0.0031087 | 0 |  | 0 | 0 |  | -0.0049501 | 0 |  | 0 | 0 |  | -0.0019972 | 0 |  | 0 | 0 |  | -0.0015068 | 0 |  | 0 | 0 | -0.0011128 | 0 |  | 0 | 0 | -0.0007894 | 0 |  | 0 | 0 | -0.00051912 | 0 |  | 0 | 0 | -0.00028989 | 0 |  | 0 | 0 | -9.3003e-05 | 0 |  | 0 | 0 | 7.7923e-05 | 0.23747 |  | 6.5186 | -1132.9846 | 0.00022771 | 0.66136 |  | 18.1543 | -3155.3456 | 0.00036005 | 1.0002 |  | 27.4554 | -4771.9242 | 0.00047782 | 1.2736 |  | 34.96 | -6076.2738 | 0.0005833 | 1.496 |  | 41.0639 | -7137.1753 | 0.00067833 | 1.6781 |  | 46.0628 | -8006.0149 | 0.00076438 | 1.8281 |  | 50.1807 | -8721.7377 | 0.00084266 | 1.9523 |  | 53.5897 | -9314.2416 | 0.00091419 | 2.0555 |  | 56.4233 | -9806.7469 | 0.0009798 | 2.1416 |  | 58.7864 | -10217.4782 | 0.0010402 | 2.2136 |  | 60.7622 | -10560.8771
107 |  | Concrete | 75 | 27.45 |  |  | -30.6939 | -174.0961 |  |  | -0.0020009 | 0 |  | 0 | 0 |  | -0.0031133 | 0 |  | 0 | 0 |  | -0.0049561 | 0 |  | 0 | 0 |  | -0.0020009 | 0 |  | 0 | 0 |  | -0.00151 | 0 |  | 0 | 0 | -0.0011158 | 0 |  | 0 | 0 | -0.00079207 | 0 |  | 0 | 0 | -0.00052157 | 0 |  | 0 | 0 | -0.00029215 | 0 |  | 0 | 0 | -9.5103e-05 | 0 |  | 0 | 0 | 7.5961e-05 | 0.23164 |  | 6.3585 | -1106.9825 | 0.00022587 | 0.65641 |  | 18.0185 | -3136.954 | 0.00035831 | 0.99597 |  | 27.3395 | -4759.6969 | 0.00047618 | 1.27 |  | 34.8606 | -6069.0908 | 0.00058175 | 1.4928 |  | 40.9783 | -7134.1572 | 0.00067685 | 1.6754 |  | 45.9888 | -8006.4632 | 0.00076297 | 1.8257 |  | 50.1165 | -8725.0913 | 0.00084132 | 1.9502 |  | 53.5339 | -9320.0455 | 0.00091291 | 2.0537 |  | 56.3748 | -9814.629 | 0.00097857 | 2.14 |  | 58.7442 | -10227.1317 | 0.001039 | 2.2122 |  | 60.7254 | -10572.0471
108 |  | Concrete | 76 | 27.45 |  |  | -27.1055 | -174.3855 |  |  | -0.0020045 | 0 |  | 0 | 0 |  | -0.0031178 | 0 |  | 0 | 0 |  | -0.0049622 | 0 |  | 0 | 0 |  | -0.0020045 | 0 |  | 0 | 0 |  | -0.0015133 | 0 |  | 0 | 0 | -0.0011187 | 0 |  | 0 | 0 | -0.00079473 | 0 |  | 0 | 0 | -0.00052401 | 0 |  | 0 | 0 | -0.0002944 | 0 |  | 0 | 0 | -9.7204e-05 | 0 |  | 0 | 0 | 7.3999e-05 | 0.22579 |  | 6.1981 | -1080.8525 | 0.00022403 | 0.65146 |  | 17.8825 | -3118.4528 | 0.00035658 | 0.99175 |  | 27.2235 | -4747.375 | 0.00047454 | 1.2663 |  | 34.7611 | -6061.8257 | 0.0005802 | 1.4897 |  | 40.8926 | -7131.0675 | 0.00067538 | 1.6727 |  | 45.9147 | -8006.8486 | 0.00076157 | 1.8234 |  | 50.0523 | -8728.3896 | 0.00083998 | 1.9482 |  | 53.4781 | -9325.8006 | 0.00091162 | 2.052 |  | 56.3262 | -9822.4679 | 0.00097734 | 2.1385 |  | 58.7018 | -10236.7468 | 0.0010378 | 2.2109 |  | 60.6884 | -10583.183
109 |  | Concrete | 77 | 27.45 |  |  | -23.5172 | -174.6748 |  |  | -0.0020081 | 0 |  | 0 | 0 |  | -0.0031224 | 0 |  | 0 | 0 |  | -0.0049682 | 0 |  | 0 | 0 |  | -0.0020081 | 0 |  | 0 | 0 |  | -0.0015165 | 0 |  | 0 | 0 | -0.0011216 | 0 |  | 0 | 0 | -0.0007974 | 0 |  | 0 | 0 | -0.00052646 | 0 |  | 0 | 0 | -0.00029666 | 0 |  | 0 | 0 | -9.9304e-05 | 0 |  | 0 | 0 | 7.2038e-05 | 0.21994 |  | 6.0375 | -1054.5944 | 0.00022219 | 0.6465 |  | 17.7464 | -3099.8418 | 0.00035485 | 0.98751 |  | 27.1073 | -4734.9585 | 0.0004729 | 1.2627 |  | 34.6614 | -6054.4784 | 0.00057865 | 1.4866 |  | 40.8067 | -7127.9061 | 0.0006739 | 1.67 |  | 45.8404 | -8007.1713 | 0.00076016 | 1.8211 |  | 49.9879 | -8731.6326 | 0.00083864 | 1.9462 |  | 53.4222 | -9331.507 | 0.00091034 | 2.0502 |  | 56.2775 | -9830.2636 | 0.00097611 | 2.137 |  | 58.6594 | -10246.3235 | 0.0010367 | 2.2095 |  | 60.6515 | -10594.2847
110 |  | Concrete | 78 | 27.45 |  |  | -19.9288 | -174.9642 |  |  | -0.0020118 | 0 |  | 0 | 0 |  | -0.0031269 | 0 |  | 0 | 0 |  | -0.0049742 | 0 |  | 0 | 0 |  | -0.0020118 | 0 |  | 0 | 0 |  | -0.0015198 | 0 |  | 0 | 0 | -0.0011245 | 0 |  | 0 | 0 | -0.00080006 | 0 |  | 0 | 0 | -0.0005289 | 0 |  | 0 | 0 | -0.00029892 | 0 |  | 0 | 0 | -0.0001014 | 0 |  | 0 | 0 | 7.0076e-05 | 0.21409 |  | 5.8767 | -1028.2081 | 0.00022035 | 0.64153 |  | 17.61 | -3081.121 | 0.00035311 | 0.98328 |  | 26.9909 | -4722.4472 | 0.00047127 | 1.2591 |  | 34.5616 | -6047.0488 | 0.00057709 | 1.4835 |  | 40.7207 | -7124.6729 | 0.00067243 | 1.6673 |  | 45.7661 | -8007.431 | 0.00075875 | 1.8187 |  | 49.9235 | -8734.8203 | 0.00083729 | 1.9441 |  | 53.3661 | -9337.1644 | 0.00090905 | 2.0484 |  | 56.2287 | -9838.0159 | 0.00097488 | 2.1354 |  | 58.6169 | -10255.8618 | 0.0010355 | 2.2082 |  | 60.6144 | -10605.3521
111 |  | Concrete | 79 | 36.6 |  |  | 35.2919 | -179.4175 |  |  | -0.0020678 | 0 |  | 0 | 0 |  | -0.0031968 | 0 |  | 0 | 0 |  | -0.0050671 | 0 |  | 0 | 0 |  | -0.0020678 | 0 |  | 0 | 0 |  | -0.0015697 | 0 |  | 0 | 0 | -0.0011696 | 0 |  | 0 | 0 | -0.00084106 | 0 |  | 0 | 0 | -0.00056653 | 0 |  | 0 | 0 | -0.00033369 | 0 |  | 0 | 0 | -0.00013372 | 0 |  | 0 | 0 | 3.9889e-05 | 0.12301 |  | 4.5023 | -807.798 | 0.00019203 | 0.56427 |  | 20.6524 | -3705.409 | 0.00032644 | 0.91733 |  | 33.5742 | -6023.807 | 0.00044606 | 1.2025 |  | 44.0109 | -7896.332 | 0.00055321 | 1.4347 |  | 52.5091 | -9421.044 | 0.00064972 | 1.6251 |  | 59.4771 | -10671.2255 | 0.00073712 | 1.7821 |  | 65.2246 | -11702.4333 | 0.00081664 | 1.9123 |  | 69.9894 | -12557.3311 | 0.00088929 | 2.0207 |  | 73.9564 | -13269.0648 | 0.00095593 | 2.1112 |  | 77.2704 | -13863.658 | 0.0010173 | 2.1871 |  | 80.0465 | -14361.7388
112 |  | Concrete | 80 | 36.6 |  |  | 30.5074 | -179.0317 |  |  | -0.002063 | 0 |  | 0 | 0 |  | -0.0031908 | 0 |  | 0 | 0 |  | -0.005059 | 0 |  | 0 | 0 |  | -0.002063 | 0 |  | 0 | 0 |  | -0.0015654 | 0 |  | 0 | 0 | -0.0011657 | 0 |  | 0 | 0 | -0.0008375 | 0 |  | 0 | 0 | -0.00056327 | 0 |  | 0 | 0 | -0.00033068 | 0 |  | 0 | 0 | -0.00013092 | 0 |  | 0 | 0 | 4.2505e-05 | 0.13097 |  | 4.7937 | -858.2167 | 0.00019448 | 0.57103 |  | 20.8996 | -3741.6984 | 0.00032875 | 0.9231 |  | 33.7853 | -6048.6452 | 0.00044825 | 1.2074 |  | 44.1921 | -7911.794 | 0.00055528 | 1.4389 |  | 52.6653 | -9428.7591 | 0.00065169 | 1.6288 |  | 59.6123 | -10672.4887 | 0.000739 | 1.7853 |  | 65.342 | -11698.2848 | 0.00081843 | 1.9151 |  | 70.0916 | -12548.615 | 0.000891 | 2.0231 |  | 74.0454 | -13256.4716 | 0.00095757 | 2.1133 |  | 77.3481 | -13847.7572 | 0.0010189 | 2.1889 |  | 80.1143 | -14343.0038
113 |  | Concrete | 81 | 36.6 |  |  | 25.7229 | -178.6458 |  |  | -0.0020581 | 0 |  | 0 | 0 |  | -0.0031847 | 0 |  | 0 | 0 |  | -0.005051 | 0 |  | 0 | 0 |  | -0.0020581 | 0 |  | 0 | 0 |  | -0.0015611 | 0 |  | 0 | 0 | -0.0011618 | 0 |  | 0 | 0 | -0.00083395 | 0 |  | 0 | 0 | -0.00056001 | 0 |  | 0 | 0 | -0.00032767 | 0 |  | 0 | 0 | -0.00012812 | 0 |  | 0 | 0 | 4.512e-05 | 0.13892 |  | 5.0845 | -908.325 | 0.00019693 | 0.57777 |  | 21.1464 | -3777.7218 | 0.00033106 | 0.92885 |  | 33.9961 | -6073.2539 | 0.00045043 | 1.2124 |  | 44.373 | -7927.0565 | 0.00055735 | 1.4432 |  | 52.8213 | -9436.3 | 0.00065366 | 1.6324 |  | 59.7473 | -10673.5991 | 0.00074087 | 1.7885 |  | 65.4591 | -11694.0019 | 0.00082022 | 1.9179 |  | 70.1935 | -12539.7801 | 0.00089271 | 2.0255 |  | 74.1342 | -13243.773 | 0.00095921 | 2.1155 |  | 77.4256 | -13831.7629 | 0.0010204 | 2.1908 |  | 80.182 | -14324.1854
114 |  | Concrete | 82 | 36.6 |  |  | 20.9385 | -178.26 |  |  | -0.0020533 | 0 |  | 0 | 0 |  | -0.0031786 | 0 |  | 0 | 0 |  | -0.005043 | 0 |  | 0 | 0 |  | -0.0020533 | 0 |  | 0 | 0 |  | -0.0015567 | 0 |  | 0 | 0 | -0.0011579 | 0 |  | 0 | 0 | -0.0008304 | 0 |  | 0 | 0 | -0.00055675 | 0 |  | 0 | 0 | -0.00032466 | 0 |  | 0 | 0 | -0.00012532 | 0 |  | 0 | 0 | 4.7736e-05 | 0.14685 |  | 5.3749 | -958.1236 | 0.00019939 | 0.5845 |  | 21.3928 | -3813.4796 | 0.00033338 | 0.9346 |  | 34.2064 | -6097.6333 | 0.00045262 | 1.2173 |  | 44.5536 | -7942.12 | 0.00055941 | 1.4475 |  | 52.9769 | -9443.6672 | 0.00065562 | 1.6361 |  | 59.882 | -10674.5572 | 0.00074275 | 1.7917 |  | 65.576 | -11689.5848 | 0.00082201 | 1.9206 |  | 70.2952 | -12530.8265 | 0.00089443 | 2.0279 |  | 74.2229 | -13230.9693 | 0.00096085 | 2.1176 |  | 77.503 | -13815.6751 | 0.001022 | 2.1926 |  | 80.2496 | -14305.2837
115 |  | Concrete | 83 | 36.6 |  |  | 16.154 | -177.8741 |  |  | -0.0020484 | 0 |  | 0 | 0 |  | -0.0031726 | 0 |  | 0 | 0 |  | -0.0050349 | 0 |  | 0 | 0 |  | -0.0020484 | 0 |  | 0 | 0 |  | -0.0015524 | 0 |  | 0 | 0 | -0.001154 | 0 |  | 0 | 0 | -0.00082685 | 0 |  | 0 | 0 | -0.00055349 | 0 |  | 0 | 0 | -0.00032164 | 0 |  | 0 | 0 | -0.00012252 | 0 |  | 0 | 0 | 5.0351e-05 | 0.15477 |  | 5.6648 | -1007.6131 | 0.00020184 | 0.59122 |  | 21.6387 | -3848.9725 | 0.00033569 | 0.94034 |  | 34.4164 | -6121.784 | 0.0004548 | 1.2222 |  | 44.7338 | -7956.9849 | 0.00056148 | 1.4517 |  | 53.1323 | -9450.861 | 0.00065759 | 1.6398 |  | 60.0164 | -10675.3631 | 0.00074462 | 1.7949 |  | 65.6927 | -11685.0338 | 0.0008238 | 1.9234 |  | 70.3967 | -12521.7546 | 0.00089614 | 2.0304 |  | 74.3113 | -13218.0608 | 0.0009625 | 2.1197 |  | 77.5801 | -13799.494 | 0.0010236 | 2.1945 |  | 80.3169 | -14286.2991
116 |  | Concrete | 84 | 36.6 |  |  | 11.3695 | -177.4883 |  |  | -0.0020436 | 0 |  | 0 | 0 |  | -0.0031665 | 0 |  | 0 | 0 |  | -0.0050269 | 0 |  | 0 | 0 |  | -0.0020436 | 0 |  | 0 | 0 |  | -0.0015481 | 0 |  | 0 | 0 | -0.0011501 | 0 |  | 0 | 0 | -0.0008233 | 0 |  | 0 | 0 | -0.00055023 | 0 |  | 0 | 0 | -0.00031863 | 0 |  | 0 | 0 | -0.00011972 | 0 |  | 0 | 0 | 5.2967e-05 | 0.16268 |  | 5.9542 | -1056.7939 | 0.0002043 | 0.59793 |  | 21.8843 | -3884.2008 | 0.000338 | 0.94607 |  | 34.626 | -6145.7063 | 0.00045698 | 1.2271 |  | 44.9137 | -7971.6515 | 0.00056355 | 1.4559 |  | 53.2874 | -9457.8817 | 0.00065956 | 1.6435 |  | 60.1505 | -10676.0173 | 0.00074649 | 1.7981 |  | 65.8091 | -11680.3491 | 0.00082559 | 1.9262 |  | 70.498 | -12512.5646 | 0.00089785 | 2.0328 |  | 74.3995 | -13205.0475 | 0.00096414 | 2.1218 |  | 77.6571 | -13783.22 | 0.0010252 | 2.1963 |  | 80.3841 | -14267.2316
117 |  | Concrete | 85 | 36.6 |  |  | 6.5851 | -177.1024 |  |  | -0.0020387 | 0 |  | 0 | 0 |  | -0.0031605 | 0 |  | 0 | 0 |  | -0.0050188 | 0 |  | 0 | 0 |  | -0.0020387 | 0 |  | 0 | 0 |  | -0.0015438 | 0 |  | 0 | 0 | -0.0011462 | 0 |  | 0 | 0 | -0.00081974 | 0 |  | 0 | 0 | -0.00054697 | 0 |  | 0 | 0 | -0.00031562 | 0 |  | 0 | 0 | -0.00011692 | 0 |  | 0 | 0 | 5.5582e-05 | 0.17058 |  | 6.2431 | -1105.6666 | 0.00020675 | 0.60463 |  | 22.1294 | -3919.1651 | 0.00034031 | 0.95178 |  | 34.8352 | -6169.4007 | 0.00045917 | 1.2321 |  | 45.0932 | -7986.1202 | 0.00056562 | 1.4602 |  | 53.4421 | -9464.7297 | 0.00066153 | 1.6471 |  | 60.2844 | -10676.52 | 0.00074837 | 1.8012 |  | 65.9253 | -11675.5311 | 0.00082738 | 1.9289 |  | 70.599 | -12503.2569 | 0.00089956 | 2.0352 |  | 74.4876 | -13191.9299 | 0.00096578 | 2.1239 |  | 77.7338 | -13766.8533 | 0.0010267 | 2.1981 |  | 80.4511 | -14248.0814
118 |  | Concrete | 86 | 36.6 |  |  | 1.8006 | -176.7166 |  |  | -0.0020338 | 0 |  | 0 | 0 |  | -0.0031544 | 0 |  | 0 | 0 |  | -0.0050108 | 0 |  | 0 | 0 |  | -0.0020338 | 0 |  | 0 | 0 |  | -0.0015394 | 0 |  | 0 | 0 | -0.0011423 | 0 |  | 0 | 0 | -0.00081619 | 0 |  | 0 | 0 | -0.00054371 | 0 |  | 0 | 0 | -0.00031261 | 0 |  | 0 | 0 | -0.00011412 | 0 |  | 0 | 0 | 5.8198e-05 | 0.17846 |  | 6.5315 | -1154.2318 | 0.0002092 | 0.61131 |  | 22.374 | -3953.8657 | 0.00034262 | 0.95749 |  | 35.0441 | -6192.8677 | 0.00046135 | 1.237 |  | 45.2724 | -8000.3914 | 0.00056769 | 1.4644 |  | 53.5966 | -9471.4053 | 0.00066349 | 1.6508 |  | 60.418 | -10676.8716 | 0.00075024 | 1.8044 |  | 66.0412 | -11670.58 | 0.00082917 | 1.9317 |  | 70.6998 | -12493.8315 | 0.00090128 | 2.0376 |  | 74.5754 | -13178.7081 | 0.00096742 | 2.126 |  | 77.8104 | -13750.3939 | 0.0010283 | 2.1999 |  | 80.5179 | -14228.8489
119 |  | Concrete | 87 | 36.6 |  |  | -2.9839 | -176.3308 |  |  | -0.002029 | 0 |  | 0 | 0 |  | -0.0031484 | 0 |  | 0 | 0 |  | -0.0050027 | 0 |  | 0 | 0 |  | -0.002029 | 0 |  | 0 | 0 |  | -0.0015351 | 0 |  | 0 | 0 | -0.0011384 | 0 |  | 0 | 0 | -0.00081264 | 0 |  | 0 | 0 | -0.00054045 | 0 |  | 0 | 0 | -0.00030959 | 0 |  | 0 | 0 | -0.00011132 | 0 |  | 0 | 0 | 6.0813e-05 | 0.18633 |  | 6.8195 | -1202.4901 | 0.00021166 | 0.61799 |  | 22.6183 | -3988.3034 | 0.00034493 | 0.96318 |  | 35.2525 | -6216.1076 | 0.00046353 | 1.2418 |  | 45.4513 | -8014.4655 | 0.00056976 | 1.4686 |  | 53.7507 | -9477.9089 | 0.00066546 | 1.6544 |  | 60.5514 | -10677.0723 | 0.00075212 | 1.8076 |  | 66.1569 | -11665.4961 | 0.00083096 | 1.9344 |  | 70.8004 | -12484.2889 | 0.00090299 | 2.04 |  | 74.663 | -13165.3823 | 0.00096906 | 2.1281 |  | 77.8868 | -13733.8423 | 0.0010299 | 2.2018 |  | 80.5845 | -14209.5341
120 |  | Concrete | 88 | 36.6 |  |  | -7.7683 | -175.9449 |  |  | -0.0020241 | 0 |  | 0 | 0 |  | -0.0031423 | 0 |  | 0 | 0 |  | -0.0049947 | 0 |  | 0 | 0 |  | -0.0020241 | 0 |  | 0 | 0 |  | -0.0015308 | 0 |  | 0 | 0 | -0.0011345 | 0 |  | 0 | 0 | -0.00080909 | 0 |  | 0 | 0 | -0.00053719 | 0 |  | 0 | 0 | -0.00030658 | 0 |  | 0 | 0 | -0.00010852 | 0 |  | 0 | 0 | 6.3429e-05 | 0.19418 |  | 7.107 | -1250.4419 | 0.00021411 | 0.62465 |  | 22.8621 | -4022.4784 | 0.00034724 | 0.96887 |  | 35.4606 | -6239.121 | 0.00046572 | 1.2467 |  | 45.6299 | -8028.3429 | 0.00057183 | 1.4728 |  | 53.9046 | -9484.2407 | 0.00066743 | 1.658 |  | 60.6845 | -10677.1225 | 0.00075399 | 1.8107 |  | 66.2723 | -11660.2797 | 0.00083275 | 1.9372 |  | 70.9008 | -12474.6292 | 0.0009047 | 2.0424 |  | 74.7504 | -13151.9529 | 0.0009707 | 2.1301 |  | 77.963 | -13717.1985 | 0.0010315 | 2.2036 |  | 80.651 | -14190.1374
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
[14 empty] | 1 | [5 empty] | 2 | [5 empty] | 3 | [5 empty] | 4 | [5 empty] | 5 |  |  |  |  | 6 |  |  |  |  | 7 |  |  |  |  | 8 |  |  |  |  | 9 |  |  |  |  | 10 |  |  |  |  | 11 |  |  |  |  | 12 |  |  |  |  | 13 |  |  |  |  | 14 |  |  |  |  | 15 |  |  |  |  | 16 |  |  |  |  | 17 |  |  |  |  | 18 |  |  |  |  | 19 |  |  |  |  | 20 |  |  |  |  | 21
|  | SUM |  | 4244.4433 | [9 empty] | 4594.6506 | 634890.6859 |  |  |  |  | 3962.3245 | 625234.423 |  |  |  |  | 3350.7768 | 595043.2801 |  |  |  |  | 4594.6506 | 634890.6859 |  |  |  |  | 5004.4255 | 627908.0367 |  |  |  | 5403.2388 | 615441.0673 |  |  |  | 5794.0857 | 597021.6599 |  |  |  | 6178.9459 | 572331.4326 |  |  |  | 6559.2201 | 541150.7807 |  |  |  | 6935.8674 | 503316.3869 |  |  |  | 7433.1675 | 437079.2349 |  |  |  | 8019.1048 | 348760.5181 |  |  |  | 8479.3375 | 277847.272 |  |  |  | 8843.5388 | 220350.4955 |  |  |  | 9133.4983 | 173341.7768 |  |  |  | 9365.3331 | 134621.7655 |  |  |  | 9551.2834 | 102529.943 |  |  |  | 9700.605 | 75780.8833 |  |  |  | 9820.5426 | 53383.5807 |  |  |  | 9916.6513 | 34550.2441 |  |  |  | 9993.4096 | 18664.3179
[14 empty] | 634890.6859 | [5 empty] | 625234.423 | [5 empty] | 595043.2801 | [5 empty] | 634890.6859 | [5 empty] | 627908.0367 |  |  |  |  | 615441.0673 |  |  |  |  | 597021.6599 |  |  |  |  | 572331.4326 |  |  |  |  | 541150.7807 |  |  |  |  | 503316.3869 |  |  |  |  | 437079.2349 |  |  |  |  | 348760.5181 |  |  |  |  | 277847.272 |  |  |  |  | 220350.4955 |  |  |  |  | 173341.7768 |  |  |  |  | 134621.7655 |  |  |  |  | 102529.943 |  |  |  |  | 75780.8833 |  |  |  |  | 53383.5807 |  |  |  |  | 34550.2441 |  |  |  |  | 18664.3179
[19 empty] | Compression Control |  |  | Tesion Control |  |  | Compression Control |  |  | Tesion Control
[19 empty] | P | M |  | P | M |  | P | M | 3015.6991 | P | M | P | M | -536.94
[15 empty] | 1 | 21 |  |  | 4594.6506 | 52907.5572 |  | 3350.7768 | 595043.2801 |  | 3015.6991 | 44628.246 | 3566.092 | 3015.6991 | 44628.246 | -536.94 | 0 | -514.8913
[15 empty] | 2 | 20 |  |  | 3962.3245 | 52102.8686 |  | 2828.1111 | 559435.117 |  | 3566.092 | 46892.5817 | 4135.1855 | 2545.3 | 41957.6338 | -514.8913 | 1.0761e-10 | -514.8913
[15 empty] | 3 | 19 |  |  | 3350.7768 | 49586.94 |  | 1319.1673 | 321104.5832 |  | 4135.1855 | 47616.8014 | 4135.1855 | 1187.2506 | 24082.8437 | -514.8913 | 1.2913e-09 | -514.8913
[15 empty] | 4 | 18 |  |  | 4594.6506 | 52907.5572 |  | -275.6427 | 48882.0565 |  | 4135.1855 | 47616.8014 | 4503.9829 | -248.0784 | 3666.1542 | -514.8913 | 1.5496e-08 | -514.8913 |  | Compression Control |  |  |  | Tesion Control
[15 empty] | 5 | 17 |  |  | 5004.4255 | 52325.6697 |  | -451.9112 | 19734.0348 |  | 4503.9829 | 47093.1027 | 4862.9149 | -406.7201 | 1480.0526 | -514.8913 | 1.8595e-07 | -514.8913 |  | P | M |  |  | P | M
[15 empty] | 6 | 16 |  |  | 5403.2388 | 51286.7556 |  | -493.9817 | 13506.9557 |  | 4862.9149 | 46158.08 | 5214.6771 | -444.5836 | 1013.0217 | -514.8913 | 2.2314e-06 | -514.8913 |  | #N/A | #N/A |  |  | -248.0784 | 3666.1542
[15 empty] | 7 | 15 |  |  | 5794.0857 | 49751.805 |  | -526.7581 | 8446.7251 |  | 5214.6771 | 44776.6245 | 5561.0513 | -474.0823 | 633.5044 | -514.8913 | 2.6777e-05 | -514.8913 |  | 360 | #N/A |  |  | 360 | 12315.7031
[15 empty] | 8 | 14 |  |  | 6178.9459 | 47694.286 |  | -552.291 | 4350.9462 |  | 5561.0513 | 42924.8574 | 5903.2981 | -497.0619 | 326.321 | -514.8913 | 0.00032132 | -514.8913 |  | #N/A | #N/A |  |  | 1187.2506 | 24082.8437
[15 empty] | 9 | 13 |  |  | 6559.2201 | 45095.8984 |  | -572.1014 | 1066.0721 |  | 5903.2981 | 40586.3086 | 6242.2807 | -514.8913 | 79.9554 | -514.8913 | 0.0038559 | -514.8913
[7 empty] | f Pn (k) | [7 empty] | 10 | 12 |  |  | 6935.8674 | 41943.0322 |  |  |  |  | 6242.2807 | 37748.729 | 6689.8508 | -514.8913 | 6.663 | -514.8913 | 0.04627 | -514.8913
[15 empty] | 11 | 11 |  |  | 7433.1675 | 36423.2696 |  |  |  |  | 6689.8508 | 32780.9426 | 7217.1943 | -514.8913 | 0.55525 | -514.8913 | 0.55525 | -514.8913
[15 empty] | 12 | 10 |  |  | 8019.1048 | 29063.3765 |  |  |  |  | 7217.1943 | 26157.0389 | 7631.4037 | -514.8913 | 0.04627 | -514.8913 | 6.663 | -514.8913
[15 empty] | 13 | 9 |  |  | 8479.3375 | 23153.9393 |  |  |  |  | 7631.4037 | 20838.5454 | 7959.1849 | -514.8913 | 0.0038559 | -514.8913 | 79.9554 | -497.0619 |  | fPmax | fM |  |  | P | M
[15 empty] | 14 | 8 |  |  | 8843.5388 | 18362.5413 |  |  |  |  | 7959.1849 | 16526.2872 | 8220.1484 | -514.8913 | 0.00032132 | -497.0619 | 326.321 | -474.0823 |  | 4729.0131 | 0 |  |  | -248.0784 | 3666.1542
[15 empty] | 15 | 7 |  |  | 9133.4983 | 14445.1481 |  |  |  |  | 8220.1484 | 13000.6333 | 8428.7998 | -514.8913 | 2.6777e-05 | -474.0823 | 633.5044 | -444.5836 |  | 4729.0131 | 47616.8014 |  |  | 0 | 7194.9202
[15 empty] | 16 | 6 |  |  | 9365.3331 | 11218.4805 |  |  |  |  | 8428.7998 | 10096.6324 | 8596.1551 | -514.8913 | 2.2314e-06 | -444.5836 | 1013.0217 | -406.7201 | [5 empty] | 1187.2506 | 24082.8437
[15 empty] | 17 | 5 |  |  | 9551.2834 | 8544.1619 |  |  |  |  | 8596.1551 | 7689.7457 | 8730.5445 | -514.8913 | 1.8595e-07 | -406.7201 | 1480.0526 | -248.0784
[15 empty] | 18 | 4 |  |  | 9700.605 | 6315.0736 |  |  |  |  | 8730.5445 | 5683.5662 | 8838.4883 | -514.8913 | 1.5496e-08 | -248.0784 | 3666.1542 | 1187.2506
[15 empty] | 19 | 3 |  |  | 9820.5426 | 4448.6317 |  |  |  |  | 8838.4883 | 4003.7686 | 8924.9862 | -514.8913 | 1.2913e-09 | 1187.2506 | 24082.8437 | 2545.3
[11 empty] | f Mn (ft-k) |  |  |  | 20 | 2 |  |  | 9916.6513 | 2879.187 |  |  |  |  | 8924.9862 | 2591.2683 | 8994.0686 | -514.8913 | 1.0761e-10 | 2545.3 | 41957.6338 | 3015.6991
[9 empty] | Solid Black Line - Tension Controlled | [5 empty] | 21 | 1 |  |  | 9993.4096 | 1555.3598 |  |  |  |  | 8994.0686 | 1399.8238 | 89940.686 | -536.94 | 0 | 3015.6991 | 44628.246
Solid Red Line - Transition
Dash Line - Compression Controlled
Tension Controlled | [10 empty] | c = | 119.9024 | in |  |  |  | c = | 83.9317 | in |  |  |  | c = | 47.961 | in |  |  |  | c = | 11.9902 | in |  |  |  | c = | -23.9805 | in |  |  | c = | -59.9512 | in |  |  | c = | -95.922 | in |  |  | c = | -131.8927 | in |  |  | c = | -167.8634 | in |  |  | c = | -203.8342 | in |  |  | c = | -239.8049 | in |  |  | c = | -275.7756 | in |  |  | c = | -311.7464 | in |  |  | c = | -347.7171 | in |  |  | c = | -383.6878 | in |  |  | c = | -419.6586 | in |  |  | c = | -455.6293 | in |  |  | c = | -491.6 | in |  |  | c = | -527.5708 | in |  |  | c = | -563.5415 | in |  |  | c = | -599.5122 | in
|  | What | Element | Area | Xoc | Yoc | X | Y |  |  | e | fc | fs | F | M |  | e | fc | fs | F | M |  | e | fc | fs | F | M |  | e | fc | fs | F | M |  | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M | e | fc | fs | F | M
1 |  | Steel | 1 | 0.062 |  |  | -35.4526 | 177.424 |  |  | 0.0023732 |  | 60 | 3.72 | 660.0172 |  | 0.001414 |  | 41.0046 | 2.5423 | 451.0618 |  | 0.00067377 |  | 19.5395 | 1.2114 | 214.9397 |  | 8.5296e-05 |  | 2.4736 | 0.15336 | 27.2101 |  | -0.00039379 |  | -11.4198 | -0.70803 | -125.621 | -0.00079138 |  | -22.9501 | -1.4229 | -252.4574 | -0.0011267 |  | -32.6729 | -2.0257 | -359.4114 | -0.0014132 |  | -40.9824 | -2.5409 | -450.8181 | -0.0016609 |  | -48.1658 | -2.9863 | -529.838 | -0.0018772 |  | -54.4376 | -3.3751 | -598.829 | -0.0020676 |  | -59.9609 | -3.7176 | -659.5866 | -0.0022366 |  | -60 | -3.72 | -660.0172 | -0.0023876 |  | -60 | -3.72 | -660.0172 | -0.0025233 |  | -60 | -3.72 | -660.0172 | -0.0026459 |  | -60 | -3.72 | -660.0172 | -0.0027573 |  | -60 | -3.72 | -660.0172 | -0.0028589 |  | -60 | -3.72 | -660.0172 | -0.0029519 |  | -60 | -3.72 | -660.0172 | -0.0030374 |  | -60 | -3.72 | -660.0172 | -0.0031163 |  | -60 | -3.72 | -660.0172 | -0.0031893 |  | -60 | -3.72 | -660.0172
2 |  | Steel | 2 | 0.062 |  |  | -30.6682 | 177.0381 |  |  | 0.0023651 |  | 60 | 3.72 | 658.5819 |  | 0.0014069 |  | 40.8013 | 2.5297 | 447.8501 |  | 0.00066757 |  | 19.3594 | 1.2003 | 212.4962 |  | 7.9724e-05 |  | 2.312 | 0.14334 | 25.3774 |  | -0.00039884 |  | -11.5664 | -0.71711 | -126.9566 | -0.00079601 |  | -23.0842 | -1.4312 | -253.3803 | -0.0011309 |  | -32.7965 | -2.0334 | -359.9863 | -0.0014171 |  | -41.097 | -2.548 | -451.0957 | -0.0016646 |  | -48.2727 | -2.9929 | -529.8584 | -0.0018806 |  | -54.5376 | -3.3813 | -598.6251 | -0.0020709 |  | -60 | -3.72 | -658.5819 | -0.0022397 |  | -60 | -3.72 | -658.5819 | -0.0023905 |  | -60 | -3.72 | -658.5819 | -0.0025261 |  | -60 | -3.72 | -658.5819 | -0.0026486 |  | -60 | -3.72 | -658.5819 | -0.0027598 |  | -60 | -3.72 | -658.5819 | -0.0028613 |  | -60 | -3.72 | -658.5819 | -0.0029542 |  | -60 | -3.72 | -658.5819 | -0.0030396 |  | -60 | -3.72 | -658.5819 | -0.0031184 |  | -60 | -3.72 | -658.5819 | -0.0031913 |  | -60 | -3.72 | -658.5819
3 |  | Steel | 3 | 0.062 |  |  | -25.8837 | 176.6523 |  |  | 0.0023571 |  | 60 | 3.72 | 657.1465 |  | 0.0013999 |  | 40.5981 | 2.5171 | 444.6482 |  | 0.00066136 |  | 19.1794 | 1.1891 | 210.0613 |  | 7.4152e-05 |  | 2.1504 | 0.13333 | 23.5524 |  | -0.00040389 |  | -11.7129 | -0.7262 | -128.2851 | -0.00080063 |  | -23.2183 | -1.4395 | -254.2968 | -0.0011352 |  | -32.9201 | -2.041 | -360.5553 | -0.0014211 |  | -41.2116 | -2.5551 | -451.3677 | -0.0016683 |  | -48.3795 | -2.9995 | -529.8738 | -0.0018841 |  | -54.6377 | -3.3875 | -598.4163 | -0.0020741 |  | -60 | -3.72 | -657.1465 | -0.0022427 |  | -60 | -3.72 | -657.1465 | -0.0023934 |  | -60 | -3.72 | -657.1465 | -0.0025288 |  | -60 | -3.72 | -657.1465 | -0.0026512 |  | -60 | -3.72 | -657.1465 | -0.0027623 |  | -60 | -3.72 | -657.1465 | -0.0028637 |  | -60 | -3.72 | -657.1465 | -0.0029565 |  | -60 | -3.72 | -657.1465 | -0.0030418 |  | -60 | -3.72 | -657.1465 | -0.0031205 |  | -60 | -3.72 | -657.1465 | -0.0031933 |  | -60 | -3.72 | -657.1465
4 |  | Steel | 4 | 0.062 |  |  | -21.0992 | 176.2665 |  |  | 0.002349 |  | 60 | 3.72 | 655.7112 |  | 0.0013929 |  | 40.3949 | 2.5045 | 441.4559 |  | 0.00065515 |  | 18.9994 | 1.178 | 207.6351 |  | 6.8581e-05 |  | 1.9888 | 0.12331 | 21.7351 |  | -0.00040895 |  | -11.8595 | -0.73529 | -129.6066 | -0.00080525 |  | -23.3524 | -1.4478 | -255.2069 | -0.0011394 |  | -33.0437 | -2.0487 | -361.1184 | -0.001425 |  | -41.3262 | -2.5622 | -451.6343 | -0.0016719 |  | -48.4864 | -3.0062 | -529.8841 | -0.0018875 |  | -54.7378 | -3.3937 | -598.2028 | -0.0020773 |  | -60 | -3.72 | -655.7112 | -0.0022458 |  | -60 | -3.72 | -655.7112 | -0.0023963 |  | -60 | -3.72 | -655.7112 | -0.0025316 |  | -60 | -3.72 | -655.7112 | -0.0026538 |  | -60 | -3.72 | -655.7112 | -0.0027648 |  | -60 | -3.72 | -655.7112 | -0.002866 |  | -60 | -3.72 | -655.7112 | -0.0029588 |  | -60 | -3.72 | -655.7112 | -0.003044 |  | -60 | -3.72 | -655.7112 | -0.0031226 |  | -60 | -3.72 | -655.7112 | -0.0031954 |  | -60 | -3.72 | -655.7112
5 |  | Steel | 5 | 0.062 |  |  | -16.3148 | 175.8806 |  |  | 0.002341 |  | 60 | 3.72 | 654.2759 |  | 0.0013859 |  | 40.1916 | 2.4919 | 438.2734 |  | 0.00064894 |  | 18.8193 | 1.1668 | 205.2174 |  | 6.3009e-05 |  | 1.8273 | 0.11329 | 19.9255 |  | -0.000414 |  | -12.006 | -0.74437 | -130.9211 | -0.00080988 |  | -23.4865 | -1.4562 | -256.1105 | -0.0011437 |  | -33.1673 | -2.0564 | -361.6756 | -0.001429 |  | -41.4408 | -2.5693 | -451.8954 | -0.0016756 |  | -48.5932 | -3.0128 | -529.8892 | -0.001891 |  | -54.8378 | -3.3999 | -597.9844 | -0.0020806 |  | -60 | -3.72 | -654.2759 | -0.0022489 |  | -60 | -3.72 | -654.2759 | -0.0023992 |  | -60 | -3.72 | -654.2759 | -0.0025343 |  | -60 | -3.72 | -654.2759 | -0.0026564 |  | -60 | -3.72 | -654.2759 | -0.0027673 |  | -60 | -3.72 | -654.2759 | -0.0028684 |  | -60 | -3.72 | -654.2759 | -0.0029611 |  | -60 | -3.72 | -654.2759 | -0.0030462 |  | -60 | -3.72 | -654.2759 | -0.0031247 |  | -60 | -3.72 | -654.2759 | -0.0031974 |  | -60 | -3.72 | -654.2759
6 |  | Steel | 6 | 0.062 |  |  | -11.5303 | 175.4948 |  |  | 0.0023329 |  | 60 | 3.72 | 652.8405 |  | 0.0013789 |  | 39.9884 | 2.4793 | 435.1006 |  | 0.00064274 |  | 18.6393 | 1.1556 | 202.8084 |  | 5.7437e-05 |  | 1.6657 | 0.10327 | 18.1237 |  | -0.00041906 |  | -12.1526 | -0.75346 | -132.2286 | -0.0008145 |  | -23.6206 | -1.4645 | -257.0077 | -0.001148 |  | -33.2908 | -2.064 | -362.2269 | -0.0014329 |  | -41.5554 | -2.5764 | -452.1511 | -0.0016793 |  | -48.7 | -3.0194 | -529.8892 | -0.0018944 |  | -54.9379 | -3.4061 | -597.7613 | -0.0020838 |  | -60 | -3.72 | -652.8405 | -0.0022519 |  | -60 | -3.72 | -652.8405 | -0.0024021 |  | -60 | -3.72 | -652.8405 | -0.0025371 |  | -60 | -3.72 | -652.8405 | -0.002659 |  | -60 | -3.72 | -652.8405 | -0.0027698 |  | -60 | -3.72 | -652.8405 | -0.0028708 |  | -60 | -3.72 | -652.8405 | -0.0029633 |  | -60 | -3.72 | -652.8405 | -0.0030484 |  | -60 | -3.72 | -652.8405 | -0.0031268 |  | -60 | -3.72 | -652.8405 | -0.0031994 |  | -60 | -3.72 | -652.8405
7 |  | Steel | 7 | 0.062 |  |  | -6.7458 | 175.1089 |  |  | 0.0023249 |  | 60 | 3.72 | 651.4052 |  | 0.0013719 |  | 39.7852 | 2.4667 | 431.9376 |  | 0.00063653 |  | 18.4593 | 1.1445 | 200.4079 |  | 5.1865e-05 |  | 1.5041 | 0.093254 | 16.3296 |  | -0.00042411 |  | -12.2992 | -0.76255 | -133.5291 | -0.00081913 |  | -23.7547 | -1.4728 | -257.8985 | -0.0011522 |  | -33.4144 | -2.0717 | -362.7723 | -0.0014369 |  | -41.67 | -2.5835 | -452.4012 | -0.001683 |  | -48.8069 | -3.026 | -529.8842 | -0.0018979 |  | -55.0379 | -3.4124 | -597.5334 | -0.0020871 |  | -60 | -3.72 | -651.4052 | -0.002255 |  | -60 | -3.72 | -651.4052 | -0.002405 |  | -60 | -3.72 | -651.4052 | -0.0025398 |  | -60 | -3.72 | -651.4052 | -0.0026617 |  | -60 | -3.72 | -651.4052 | -0.0027723 |  | -60 | -3.72 | -651.4052 | -0.0028732 |  | -60 | -3.72 | -651.4052 | -0.0029656 |  | -60 | -3.72 | -651.4052 | -0.0030506 |  | -60 | -3.72 | -651.4052 | -0.0031289 |  | -60 | -3.72 | -651.4052 | -0.0032014 |  | -60 | -3.72 | -651.4052
8 |  | Steel | 8 | 0.062 |  |  | -1.9614 | 174.7231 |  |  | 0.0023168 |  | 60 | 3.72 | 649.9698 |  | 0.0013649 |  | 39.5819 | 2.4541 | 428.7842 |  | 0.00063032 |  | 18.2793 | 1.1333 | 198.0161 |  | 4.6294e-05 |  | 1.3425 | 0.083236 | 14.5432 |  | -0.00042916 |  | -12.4457 | -0.77164 | -134.8225 | -0.00082375 |  | -23.8888 | -1.4811 | -258.7829 | -0.0011565 |  | -33.538 | -2.0794 | -363.3117 | -0.0014408 |  | -41.7846 | -2.5906 | -452.6459 | -0.0016867 |  | -48.9137 | -3.0327 | -529.874 | -0.0019013 |  | -55.138 | -3.4186 | -597.3007 | -0.0020903 |  | -60 | -3.72 | -649.9698 | -0.0022581 |  | -60 | -3.72 | -649.9698 | -0.0024079 |  | -60 | -3.72 | -649.9698 | -0.0025426 |  | -60 | -3.72 | -649.9698 | -0.0026643 |  | -60 | -3.72 | -649.9698 | -0.0027748 |  | -60 | -3.72 | -649.9698 | -0.0028756 |  | -60 | -3.72 | -649.9698 | -0.0029679 |  | -60 | -3.72 | -649.9698 | -0.0030528 |  | -60 | -3.72 | -649.9698 | -0.0031311 |  | -60 | -3.72 | -649.9698 | -0.0032035 |  | -60 | -3.72 | -649.9698
9 |  | Steel | 9 | 0.062 |  |  | 2.8231 | 174.3372 |  |  | 0.0023088 |  | 60 | 3.72 | 648.5345 |  | 0.0013579 |  | 39.3787 | 2.4415 | 425.6406 |  | 0.00062411 |  | 18.0992 | 1.1222 | 195.6329 |  | 4.0722e-05 |  | 1.1809 | 0.073218 | 12.7646 |  | -0.00043422 |  | -12.5923 | -0.78072 | -136.109 | -0.00082837 |  | -24.0229 | -1.4894 | -259.6609 | -0.0011607 |  | -33.6616 | -2.087 | -363.8453 | -0.0014448 |  | -41.8992 | -2.5978 | -452.885 | -0.0016904 |  | -49.0206 | -3.0393 | -529.8587 | -0.0019048 |  | -55.2381 | -3.4248 | -597.0632 | -0.0020936 |  | -60 | -3.72 | -648.5345 | -0.0022611 |  | -60 | -3.72 | -648.5345 | -0.0024108 |  | -60 | -3.72 | -648.5345 | -0.0025453 |  | -60 | -3.72 | -648.5345 | -0.0026669 |  | -60 | -3.72 | -648.5345 | -0.0027773 |  | -60 | -3.72 | -648.5345 | -0.002878 |  | -60 | -3.72 | -648.5345 | -0.0029702 |  | -60 | -3.72 | -648.5345 | -0.003055 |  | -60 | -3.72 | -648.5345 | -0.0031332 |  | -60 | -3.72 | -648.5345 | -0.0032055 |  | -60 | -3.72 | -648.5345
10 |  | Steel | 10 | 0.062 |  |  | 7.6076 | 173.9514 |  |  | 0.0023008 |  | 60 | 3.72 | 647.0992 |  | 0.0013509 |  | 39.1754 | 2.4289 | 422.5067 |  | 0.0006179 |  | 17.9192 | 1.111 | 193.2583 |  | 3.515e-05 |  | 1.0194 | 0.0632 | 10.9937 |  | -0.00043927 |  | -12.7389 | -0.78981 | -137.3884 | -0.000833 |  | -24.157 | -1.4977 | -260.5325 | -0.001165 |  | -33.7852 | -2.0947 | -364.3729 | -0.0014488 |  | -42.0138 | -2.6049 | -453.1187 | -0.001694 |  | -49.1274 | -3.0459 | -529.8382 | -0.0019082 |  | -55.3381 | -3.431 | -596.8209 | -0.0020968 |  | -60 | -3.72 | -647.0992 | -0.0022642 |  | -60 | -3.72 | -647.0992 | -0.0024137 |  | -60 | -3.72 | -647.0992 | -0.0025481 |  | -60 | -3.72 | -647.0992 | -0.0026695 |  | -60 | -3.72 | -647.0992 | -0.0027798 |  | -60 | -3.72 | -647.0992 | -0.0028804 |  | -60 | -3.72 | -647.0992 | -0.0029725 |  | -60 | -3.72 | -647.0992 | -0.0030572 |  | -60 | -3.72 | -647.0992 | -0.0031353 |  | -60 | -3.72 | -647.0992 | -0.0032075 |  | -60 | -3.72 | -647.0992
11 |  | Steel | 11 | 0.062 |  |  | 40.7001 | 171.2826 |  |  | 0.0022451 |  | 60 | 3.72 | 637.1714 |  | 0.0013024 |  | 37.7698 | 2.3417 | 401.0967 |  | 0.00057497 |  | 16.674 | 1.0338 | 177.0698 |  | -3.3881e-06 |  | -0.098254 | -0.0060918 | -1.0434 |  | -0.00047423 |  | -13.7526 | -0.85266 | -146.0459 | -0.00086498 |  | -25.0845 | -1.5552 | -266.3852 | -0.0011945 |  | -34.64 | -2.1477 | -367.8605 | -0.0014761 |  | -42.8065 | -2.654 | -454.585 | -0.0017195 |  | -49.8664 | -3.0917 | -529.5571 | -0.0019321 |  | -56.0302 | -3.4739 | -595.0141 | -0.0021193 |  | -60 | -3.72 | -637.1714 | -0.0022854 |  | -60 | -3.72 | -637.1714 | -0.0024337 |  | -60 | -3.72 | -637.1714 | -0.0025671 |  | -60 | -3.72 | -637.1714 | -0.0026876 |  | -60 | -3.72 | -637.1714 | -0.0027971 |  | -60 | -3.72 | -637.1714 | -0.0028969 |  | -60 | -3.72 | -637.1714 | -0.0029883 |  | -60 | -3.72 | -637.1714 | -0.0030724 |  | -60 | -3.72 | -637.1714 | -0.0031499 |  | -60 | -3.72 | -637.1714 | -0.0032216 |  | -60 | -3.72 | -637.1714
12 |  | Steel | 12 | 0.062 |  |  | 38.3079 | 171.4756 |  |  | 0.0022491 |  | 60 | 3.72 | 637.8891 |  | 0.0013059 |  | 37.8714 | 2.348 | 402.6289 |  | 0.00057807 |  | 16.764 | 1.0394 | 178.2263 |  | -6.022e-07 |  | -0.017464 | -0.0010827 | -0.18567 |  | -0.0004717 |  | -13.6793 | -0.84812 | -145.4313 | -0.00086267 |  | -25.0174 | -1.5511 | -265.9724 | -0.0011924 |  | -34.5782 | -2.1438 | -367.6178 | -0.0014741 |  | -42.7492 | -2.6505 | -454.4878 | -0.0017177 |  | -49.8129 | -3.0884 | -529.5856 | -0.0019304 |  | -55.9802 | -3.4708 | -595.1524 | -0.0021176 |  | -60 | -3.72 | -637.8891 | -0.0022838 |  | -60 | -3.72 | -637.8891 | -0.0024323 |  | -60 | -3.72 | -637.8891 | -0.0025657 |  | -60 | -3.72 | -637.8891 | -0.0026863 |  | -60 | -3.72 | -637.8891 | -0.0027958 |  | -60 | -3.72 | -637.8891 | -0.0028957 |  | -60 | -3.72 | -637.8891 | -0.0029872 |  | -60 | -3.72 | -637.8891 | -0.0030713 |  | -60 | -3.72 | -637.8891 | -0.0031488 |  | -60 | -3.72 | -637.8891 | -0.0032206 |  | -60 | -3.72 | -637.8891
13 |  | Steel | 13 | 0.062 |  |  | 35.9157 | 171.6685 |  |  | 0.0022532 |  | 60 | 3.72 | 638.6067 |  | 0.0013094 |  | 37.973 | 2.3543 | 404.1634 |  | 0.00058117 |  | 16.854 | 1.0449 | 179.3849 |  | 2.1837e-06 |  | 0.063327 | 0.0039263 | 0.67402 |  | -0.00046917 |  | -13.606 | -0.84357 | -144.8149 | -0.00086036 |  | -24.9504 | -1.5469 | -265.558 | -0.0011902 |  | -34.5164 | -2.14 | -367.3737 | -0.0014721 |  | -42.6919 | -2.6469 | -454.3892 | -0.0017158 |  | -49.7595 | -3.0851 | -529.6128 | -0.0019286 |  | -55.9301 | -3.4677 | -595.2895 | -0.002116 |  | -60 | -3.72 | -638.6067 | -0.0022823 |  | -60 | -3.72 | -638.6067 | -0.0024308 |  | -60 | -3.72 | -638.6067 | -0.0025644 |  | -60 | -3.72 | -638.6067 | -0.002685 |  | -60 | -3.72 | -638.6067 | -0.0027946 |  | -60 | -3.72 | -638.6067 | -0.0028945 |  | -60 | -3.72 | -638.6067 | -0.002986 |  | -60 | -3.72 | -638.6067 | -0.0030702 |  | -60 | -3.72 | -638.6067 | -0.0031478 |  | -60 | -3.72 | -638.6067 | -0.0032196 |  | -60 | -3.72 | -638.6067
14 |  | Steel | 14 | 0.062 |  |  | 33.5234 | 171.8614 |  |  | 0.0022572 |  | 60 | 3.72 | 639.3244 |  | 0.0013129 |  | 38.0746 | 2.3606 | 405.7004 |  | 0.00058428 |  | 16.944 | 1.0505 | 180.5456 |  | 4.9696e-06 |  | 0.14412 | 0.0089353 | 1.5356 |  | -0.00046665 |  | -13.5327 | -0.83903 | -144.1968 | -0.00085805 |  | -24.8833 | -1.5428 | -265.142 | -0.0011881 |  | -34.4546 | -2.1362 | -367.1281 | -0.0014702 |  | -42.6346 | -2.6433 | -454.2892 | -0.001714 |  | -49.7061 | -3.0818 | -529.6388 | -0.0019269 |  | -55.8801 | -3.4646 | -595.4254 | -0.0021144 |  | -60 | -3.72 | -639.3244 | -0.0022808 |  | -60 | -3.72 | -639.3244 | -0.0024294 |  | -60 | -3.72 | -639.3244 | -0.002563 |  | -60 | -3.72 | -639.3244 | -0.0026837 |  | -60 | -3.72 | -639.3244 | -0.0027933 |  | -60 | -3.72 | -639.3244 | -0.0028933 |  | -60 | -3.72 | -639.3244 | -0.0029849 |  | -60 | -3.72 | -639.3244 | -0.0030691 |  | -60 | -3.72 | -639.3244 | -0.0031467 |  | -60 | -3.72 | -639.3244 | -0.0032185 |  | -60 | -3.72 | -639.3244
15 |  | Steel | 15 | 0.062 |  |  | 31.1312 | 172.0543 |  |  | 0.0022612 |  | 60 | 3.72 | 640.0421 |  | 0.0013164 |  | 38.1762 | 2.3669 | 407.2398 |  | 0.00058738 |  | 17.0341 | 1.0561 | 181.7085 |  | 7.7555e-06 |  | 0.22491 | 0.013944 | 2.3992 |  | -0.00046412 |  | -13.4595 | -0.83449 | -143.577 | -0.00085573 |  | -24.8163 | -1.5386 | -264.7244 | -0.001186 |  | -34.3928 | -2.1324 | -366.8811 | -0.0014682 |  | -42.5773 | -2.6398 | -454.1879 | -0.0017122 |  | -49.6527 | -3.0785 | -529.6635 | -0.0019252 |  | -55.8301 | -3.4615 | -595.5601 | -0.0021128 |  | -60 | -3.72 | -640.0421 | -0.0022792 |  | -60 | -3.72 | -640.0421 | -0.002428 |  | -60 | -3.72 | -640.0421 | -0.0025616 |  | -60 | -3.72 | -640.0421 | -0.0026824 |  | -60 | -3.72 | -640.0421 | -0.0027921 |  | -60 | -3.72 | -640.0421 | -0.0028921 |  | -60 | -3.72 | -640.0421 | -0.0029838 |  | -60 | -3.72 | -640.0421 | -0.003068 |  | -60 | -3.72 | -640.0421 | -0.0031457 |  | -60 | -3.72 | -640.0421 | -0.0032175 |  | -60 | -3.72 | -640.0421
16 |  | Steel | 16 | 0.062 |  |  | 28.739 | 172.2472 |  |  | 0.0022652 |  | 60 | 3.72 | 640.7597 |  | 0.0013199 |  | 38.2778 | 2.3732 | 408.7816 |  | 0.00059049 |  | 17.1241 | 1.0617 | 182.8735 |  | 1.0541e-05 |  | 0.3057 | 0.018953 | 3.2647 |  | -0.00046159 |  | -13.3862 | -0.82994 | -142.9554 | -0.00085342 |  | -24.7492 | -1.5345 | -264.3052 | -0.0011838 |  | -34.331 | -2.1285 | -366.6325 | -0.0014662 |  | -42.52 | -2.6362 | -454.0853 | -0.0017103 |  | -49.5993 | -3.0752 | -529.6869 | -0.0019235 |  | -55.7801 | -3.4584 | -595.6936 | -0.0021111 |  | -60 | -3.72 | -640.7597 | -0.0022777 |  | -60 | -3.72 | -640.7597 | -0.0024265 |  | -60 | -3.72 | -640.7597 | -0.0025602 |  | -60 | -3.72 | -640.7597 | -0.0026811 |  | -60 | -3.72 | -640.7597 | -0.0027908 |  | -60 | -3.72 | -640.7597 | -0.0028909 |  | -60 | -3.72 | -640.7597 | -0.0029826 |  | -60 | -3.72 | -640.7597 | -0.0030669 |  | -60 | -3.72 | -640.7597 | -0.0031446 |  | -60 | -3.72 | -640.7597 | -0.0032165 |  | -60 | -3.72 | -640.7597
17 |  | Steel | 17 | 0.062 |  |  | 26.3467 | 172.4402 |  |  | 0.0022692 |  | 60 | 3.72 | 641.4774 |  | 0.0013234 |  | 38.3795 | 2.3795 | 410.3259 |  | 0.00059359 |  | 17.2141 | 1.0673 | 184.0407 |  | 1.3327e-05 |  | 0.38649 | 0.023962 | 4.1321 |  | -0.00045907 |  | -13.3129 | -0.8254 | -142.332 | -0.00085111 |  | -24.6822 | -1.5303 | -263.8843 | -0.0011817 |  | -34.2693 | -2.1247 | -366.3825 | -0.0014642 |  | -42.4627 | -2.6327 | -453.9812 | -0.0017085 |  | -49.5458 | -3.0718 | -529.709 | -0.0019217 |  | -55.73 | -3.4553 | -595.8259 | -0.0021095 |  | -60 | -3.72 | -641.4774 | -0.0022762 |  | -60 | -3.72 | -641.4774 | -0.0024251 |  | -60 | -3.72 | -641.4774 | -0.0025589 |  | -60 | -3.72 | -641.4774 | -0.0026798 |  | -60 | -3.72 | -641.4774 | -0.0027896 |  | -60 | -3.72 | -641.4774 | -0.0028897 |  | -60 | -3.72 | -641.4774 | -0.0029815 |  | -60 | -3.72 | -641.4774 | -0.0030658 |  | -60 | -3.72 | -641.4774 | -0.0031435 |  | -60 | -3.72 | -641.4774 | -0.0032155 |  | -60 | -3.72 | -641.4774
18 |  | Steel | 18 | 0.062 |  |  | 23.9545 | 172.6331 |  |  | 0.0022733 |  | 60 | 3.72 | 642.1951 |  | 0.0013269 |  | 38.4811 | 2.3858 | 411.8725 |  | 0.00059669 |  | 17.3041 | 1.0729 | 185.2101 |  | 1.6113e-05 |  | 0.46728 | 0.028971 | 5.0014 |  | -0.00045654 |  | -13.2396 | -0.82086 | -141.7069 | -0.0008488 |  | -24.6151 | -1.5261 | -263.4619 | -0.0011796 |  | -34.2075 | -2.1209 | -366.131 | -0.0014623 |  | -42.4054 | -2.6291 | -453.8758 | -0.0017066 |  | -49.4924 | -3.0685 | -529.7299 | -0.00192 |  | -55.68 | -3.4522 | -595.957 | -0.0021079 |  | -60 | -3.72 | -642.1951 | -0.0022746 |  | -60 | -3.72 | -642.1951 | -0.0024236 |  | -60 | -3.72 | -642.1951 | -0.0025575 |  | -60 | -3.72 | -642.1951 | -0.0026785 |  | -60 | -3.72 | -642.1951 | -0.0027883 |  | -60 | -3.72 | -642.1951 | -0.0028885 |  | -60 | -3.72 | -642.1951 | -0.0029803 |  | -60 | -3.72 | -642.1951 | -0.0030647 |  | -60 | -3.72 | -642.1951 | -0.0031425 |  | -60 | -3.72 | -642.1951 | -0.0032145 |  | -60 | -3.72 | -642.1951
19 |  | Steel | 19 | 0.062 |  |  | 21.5623 | 172.826 |  |  | 0.0022773 |  | 60 | 3.72 | 642.9128 |  | 0.0013304 |  | 38.5827 | 2.3921 | 413.4217 |  | 0.0005998 |  | 17.3941 | 1.0784 | 186.3816 |  | 1.8899e-05 |  | 0.54807 | 0.03398 | 5.8727 |  | -0.00045401 |  | -13.1663 | -0.81631 | -141.0801 | -0.00084649 |  | -24.5481 | -1.522 | -263.0379 | -0.0011774 |  | -34.1457 | -2.117 | -365.8781 | -0.0014603 |  | -42.3481 | -2.6256 | -453.769 | -0.0017048 |  | -49.439 | -3.0652 | -529.7495 | -0.0019183 |  | -55.63 | -3.4491 | -596.0869 | -0.0021063 |  | -60 | -3.72 | -642.9128 | -0.0022731 |  | -60 | -3.72 | -642.9128 | -0.0024222 |  | -60 | -3.72 | -642.9128 | -0.0025561 |  | -60 | -3.72 | -642.9128 | -0.0026772 |  | -60 | -3.72 | -642.9128 | -0.0027871 |  | -60 | -3.72 | -642.9128 | -0.0028874 |  | -60 | -3.72 | -642.9128 | -0.0029792 |  | -60 | -3.72 | -642.9128 | -0.0030636 |  | -60 | -3.72 | -642.9128 | -0.0031414 |  | -60 | -3.72 | -642.9128 | -0.0032135 |  | -60 | -3.72 | -642.9128
20 |  | Steel | 20 | 0.062 |  |  | 19.17 | 173.0189 |  |  | 0.0022813 |  | 60 | 3.72 | 643.6304 |  | 0.0013339 |  | 38.6843 | 2.3984 | 414.9732 |  | 0.0006029 |  | 17.4841 | 1.084 | 187.5553 |  | 2.1685e-05 |  | 0.62886 | 0.038989 | 6.7459 |  | -0.00045148 |  | -13.0931 | -0.81177 | -140.4514 | -0.00084417 |  | -24.481 | -1.5178 | -262.6123 | -0.0011753 |  | -34.0839 | -2.1132 | -365.6236 | -0.0014583 |  | -42.2908 | -2.622 | -453.6608 | -0.001703 |  | -49.3856 | -3.0619 | -529.7678 | -0.0019165 |  | -55.5799 | -3.446 | -596.2157 | -0.0021047 |  | -60 | -3.72 | -643.6304 | -0.0022716 |  | -60 | -3.72 | -643.6304 | -0.0024207 |  | -60 | -3.72 | -643.6304 | -0.0025547 |  | -60 | -3.72 | -643.6304 | -0.0026759 |  | -60 | -3.72 | -643.6304 | -0.0027858 |  | -60 | -3.72 | -643.6304 | -0.0028862 |  | -60 | -3.72 | -643.6304 | -0.002978 |  | -60 | -3.72 | -643.6304 | -0.0030625 |  | -60 | -3.72 | -643.6304 | -0.0031404 |  | -60 | -3.72 | -643.6304 | -0.0032125 |  | -60 | -3.72 | -643.6304
21 |  | Steel | 21 | 0.22 |  |  | 14.3084 | 177.424 |  |  | 0.0023732 |  | 60 | 13.2 | 2341.9966 |  | 0.001414 |  | 41.0046 | 9.021 | 1600.542 |  | 0.00067377 |  | 19.5395 | 4.2987 | 762.6893 |  | 8.5296e-05 |  | 2.4736 | 0.54419 | 96.5521 |  | -0.00039379 |  | -11.4198 | -2.5124 | -445.752 | -0.00079138 |  | -22.9501 | -5.049 | -895.8167 | -0.0011267 |  | -32.6729 | -7.188 | -1275.3306 | -0.0014132 |  | -40.9824 | -9.0161 | -1599.6772 | -0.0016609 |  | -48.1658 | -10.5965 | -1880.0702 | -0.0018772 |  | -54.4376 | -11.9763 | -2124.8773 | -0.0020676 |  | -59.9609 | -13.1914 | -2340.4687 | -0.0022366 |  | -60 | -13.2 | -2341.9966 | -0.0023876 |  | -60 | -13.2 | -2341.9966 | -0.0025233 |  | -60 | -13.2 | -2341.9966 | -0.0026459 |  | -60 | -13.2 | -2341.9966 | -0.0027573 |  | -60 | -13.2 | -2341.9966 | -0.0028589 |  | -60 | -13.2 | -2341.9966 | -0.0029519 |  | -60 | -13.2 | -2341.9966 | -0.0030374 |  | -60 | -13.2 | -2341.9966 | -0.0031163 |  | -60 | -13.2 | -2341.9966 | -0.0031893 |  | -60 | -13.2 | -2341.9966
22 |  | Steel | 22 | 0.22 |  |  | 13.9868 | 173.4369 |  |  | 0.00229 |  | 60 | 13.2 | 2289.3675 |  | 0.0013415 |  | 38.9045 | 8.559 | 1484.4439 |  | 0.00060963 |  | 17.6792 | 3.8894 | 674.5681 |  | 2.7721e-05 |  | 0.80391 | 0.17686 | 30.674 |  | -0.00044601 |  | -12.9343 | -2.8455 | -493.5218 | -0.00083916 |  | -24.3358 | -5.3539 | -928.5582 | -0.0011707 |  | -33.95 | -7.469 | -1295.3998 | -0.001454 |  | -42.1667 | -9.2767 | -1608.916 | -0.001699 |  | -49.2698 | -10.8394 | -1879.9463 | -0.0019128 |  | -55.4715 | -12.2037 | -2116.579 | -0.0021011 |  | -60 | -13.2 | -2289.3675 | -0.0022683 |  | -60 | -13.2 | -2289.3675 | -0.0024176 |  | -60 | -13.2 | -2289.3675 | -0.0025518 |  | -60 | -13.2 | -2289.3675 | -0.002673 |  | -60 | -13.2 | -2289.3675 | -0.0027831 |  | -60 | -13.2 | -2289.3675 | -0.0028836 |  | -60 | -13.2 | -2289.3675 | -0.0029756 |  | -60 | -13.2 | -2289.3675 | -0.0030601 |  | -60 | -13.2 | -2289.3675 | -0.0031381 |  | -60 | -13.2 | -2289.3675 | -0.0032103 |  | -60 | -13.2 | -2289.3675
23 |  | Steel | 23 | 0.22 |  |  | 13.6653 | 169.4499 |  |  | 0.0022069 |  | 60 | 13.2 | 2236.7383 |  | 0.0012691 |  | 36.8044 | 8.097 | 1372.0299 |  | 0.00054548 |  | 15.8189 | 3.4801 | 589.7105 |  | -2.9854e-05 |  | -0.86577 | -0.19047 | -32.2749 |  | -0.00049823 |  | -14.4488 | -3.1787 | -538.6348 | -0.00088695 |  | -25.7214 | -5.6587 | -958.8689 | -0.0012147 |  | -35.2271 | -7.75 | -1313.2285 | -0.0014949 |  | -43.3509 | -9.5372 | -1616.0772 | -0.001737 |  | -50.3739 | -11.0822 | -1877.8857 | -0.0019485 |  | -56.5055 | -12.4312 | -2106.4668 | -0.0021347 |  | -60 | -13.2 | -2236.7383 | -0.0022999 |  | -60 | -13.2 | -2236.7383 | -0.0024475 |  | -60 | -13.2 | -2236.7383 | -0.0025802 |  | -60 | -13.2 | -2236.7383 | -0.0027001 |  | -60 | -13.2 | -2236.7383 | -0.002809 |  | -60 | -13.2 | -2236.7383 | -0.0029083 |  | -60 | -13.2 | -2236.7383 | -0.0029992 |  | -60 | -13.2 | -2236.7383 | -0.0030828 |  | -60 | -13.2 | -2236.7383 | -0.0031599 |  | -60 | -13.2 | -2236.7383 | -0.0032312 |  | -60 | -13.2 | -2236.7383
24 |  | Steel | 24 | 0.22 |  |  | 13.3438 | 165.4628 |  |  | 0.0021238 |  | 60 | 13.2 | 2184.1092 |  | 0.0011967 |  | 34.7043 | 7.6349 | 1263.3001 |  | 0.00048133 |  | 13.9585 | 3.0709 | 508.1164 |  | -8.7429e-05 |  | -2.5354 | -0.5578 | -92.2947 |  | -0.00055046 |  | -15.9632 | -3.5119 | -581.0909 | -0.00093473 |  | -27.1071 | -5.9636 | -986.7487 | -0.0012588 |  | -36.5041 | -8.0309 | -1328.8169 | -0.0015357 |  | -44.5352 | -9.7977 | -1621.161 | -0.0017751 |  | -51.4779 | -11.3251 | -1873.8883 | -0.0019841 |  | -57.5395 | -12.6587 | -2094.5408 | -0.0021682 |  | -60 | -13.2 | -2184.1092 | -0.0023315 |  | -60 | -13.2 | -2184.1092 | -0.0024775 |  | -60 | -13.2 | -2184.1092 | -0.0026086 |  | -60 | -13.2 | -2184.1092 | -0.0027271 |  | -60 | -13.2 | -2184.1092 | -0.0028348 |  | -60 | -13.2 | -2184.1092 | -0.0029329 |  | -60 | -13.2 | -2184.1092 | -0.0030228 |  | -60 | -13.2 | -2184.1092 | -0.0031055 |  | -60 | -13.2 | -2184.1092 | -0.0031817 |  | -60 | -13.2 | -2184.1092 | -0.0032522 |  | -60 | -13.2 | -2184.1092
25 |  | Steel | 25 | 0.15033 |  |  | 12.8534 | 159.3826 |  |  | 0.001997 |  | 57.9127 | 8.7062 | 1387.6168 |  | 0.0010863 |  | 31.5017 | 4.7358 | 754.7966 |  | 0.0003835 |  | 11.1216 | 1.6719 | 266.4786 |  | -0.00017523 |  | -5.0817 | -0.76395 | -121.76 |  | -0.0006301 |  | -18.2728 | -2.747 | -437.8261 | -0.0010076 |  | -29.2203 | -4.3928 | -700.1331 | -0.0013259 |  | -38.4517 | -5.7806 | -921.3218 | -0.001598 |  | -46.3412 | -6.9666 | -1110.3577 | -0.0018332 |  | -53.1615 | -7.9919 | -1273.7766 | -0.0020385 |  | -59.1162 | -8.8871 | -1416.4552 | -0.0022193 |  | -60 | -9.02 | -1437.6307 | -0.0023798 |  | -60 | -9.02 | -1437.6307 | -0.0025231 |  | -60 | -9.02 | -1437.6307 | -0.002652 |  | -60 | -9.02 | -1437.6307 | -0.0027684 |  | -60 | -9.02 | -1437.6307 | -0.0028742 |  | -60 | -9.02 | -1437.6307 | -0.0029706 |  | -60 | -9.02 | -1437.6307 | -0.0030589 |  | -60 | -9.02 | -1437.6307 | -0.0031401 |  | -60 | -9.02 | -1437.6307 | -0.003215 |  | -60 | -9.02 | -1437.6307 | -0.0032843 |  | -60 | -9.02 | -1437.6307
26 |  | Steel | 26 | 0.15033 |  |  | 12.1943 | 151.2091 |  |  | 0.0018266 |  | 52.9705 | 7.9632 | 1204.1131 |  | 0.00093781 |  | 27.1965 | 4.0885 | 618.2251 |  | 0.000252 |  | 7.3079 | 1.0986 | 166.1225 |  | -0.00029326 |  | -8.5045 | -1.2785 | -193.323 |  | -0.00073716 |  | -21.3775 | -3.2138 | -485.9485 | -0.0011055 |  | -32.0609 | -4.8198 | -728.8019 | -0.0014162 |  | -41.0697 | -6.1741 | -933.5864 | -0.0016817 |  | -48.7689 | -7.3316 | -1108.6027 | -0.0019112 |  | -55.4247 | -8.3322 | -1259.9019 | -0.0021116 |  | -60 | -9.02 | -1363.906 | -0.0022881 |  | -60 | -9.02 | -1363.906 | -0.0024446 |  | -60 | -9.02 | -1363.906 | -0.0025845 |  | -60 | -9.02 | -1363.906 | -0.0027103 |  | -60 | -9.02 | -1363.906 | -0.0028239 |  | -60 | -9.02 | -1363.906 | -0.0029271 |  | -60 | -9.02 | -1363.906 | -0.0030212 |  | -60 | -9.02 | -1363.906 | -0.0031074 |  | -60 | -9.02 | -1363.906 | -0.0031866 |  | -60 | -9.02 | -1363.906 | -0.0032597 |  | -60 | -9.02 | -1363.906 | -0.0033273 |  | -60 | -9.02 | -1363.906
27 |  | Steel | 27 | 0.15033 |  |  | 11.5351 | 143.0356 |  |  | 0.0016561 |  | 48.0283 | 7.2203 | 1032.7547 |  | 0.00078936 |  | 22.8914 | 3.4413 | 492.2335 |  | 0.00012049 |  | 3.4943 | 0.52531 | 75.1384 |  | -0.00041129 |  | -11.9274 | -1.7931 | -256.4743 |  | -0.00084421 |  | -24.4822 | -3.6805 | -526.4411 | -0.0012035 |  | -34.9016 | -5.2469 | -750.4898 | -0.0015065 |  | -43.6877 | -6.5677 | -939.4173 | -0.0017654 |  | -51.1966 | -7.6966 | -1100.8817 | -0.0019892 |  | -57.688 | -8.6724 | -1240.4653 | -0.0021847 |  | -60 | -9.02 | -1290.1814 | -0.0023568 |  | -60 | -9.02 | -1290.1814 | -0.0025095 |  | -60 | -9.02 | -1290.1814 | -0.0026459 |  | -60 | -9.02 | -1290.1814 | -0.0027686 |  | -60 | -9.02 | -1290.1814 | -0.0028794 |  | -60 | -9.02 | -1290.1814 | -0.00298 |  | -60 | -9.02 | -1290.1814 | -0.0030718 |  | -60 | -9.02 | -1290.1814 | -0.0031559 |  | -60 | -9.02 | -1290.1814 | -0.0032331 |  | -60 | -9.02 | -1290.1814 | -0.0033044 |  | -60 | -9.02 | -1290.1814 | -0.0033704 |  | -60 | -9.02 | -1290.1814
28 |  | Steel | 28 | 0.15033 |  |  | 10.876 | 134.8622 |  |  | 0.0014857 |  | 43.0862 | 6.4773 | 873.5416 |  | 0.0006409 |  | 18.5862 | 2.7941 | 376.8218 |  | -1.1011e-05 |  | -0.31931 | -0.048003 | -6.4738 |  | -0.00052932 |  | -15.3502 | -2.3076 | -311.2141 |  | -0.00095127 |  | -27.5869 | -4.1472 | -559.304 | -0.0013015 |  | -37.7422 | -5.6739 | -765.1968 | -0.0015967 |  | -46.3057 | -6.9613 | -938.8145 | -0.0018491 |  | -53.6243 | -8.0615 | -1087.1945 | -0.0020673 |  | -59.9512 | -9.0127 | -1215.4669 | -0.0022578 |  | -60 | -9.02 | -1216.4567 | -0.0024255 |  | -60 | -9.02 | -1216.4567 | -0.0025744 |  | -60 | -9.02 | -1216.4567 | -0.0027073 |  | -60 | -9.02 | -1216.4567 | -0.0028269 |  | -60 | -9.02 | -1216.4567 | -0.0029349 |  | -60 | -9.02 | -1216.4567 | -0.003033 |  | -60 | -9.02 | -1216.4567 | -0.0031224 |  | -60 | -9.02 | -1216.4567 | -0.0032043 |  | -60 | -9.02 | -1216.4567 | -0.0032797 |  | -60 | -9.02 | -1216.4567 | -0.0033491 |  | -60 | -9.02 | -1216.4567 | -0.0034134 |  | -60 | -9.02 | -1216.4567
29 |  | Steel | 29 | 0.15033 |  |  | 10.2168 | 126.6887 |  |  | 0.0013153 |  | 38.144 | 5.7343 | 726.4737 |  | 0.00049245 |  | 14.281 | 2.1469 | 271.9899 |  | -0.00014252 |  | -4.1329 | -0.62132 | -78.7141 |  | -0.00064735 |  | -18.773 | -2.8222 | -357.5424 |  | -0.0010583 |  | -30.6916 | -4.614 | -584.5372 | -0.0013994 |  | -40.5829 | -6.101 | -772.9229 | -0.001687 |  | -48.9237 | -7.3549 | -931.7779 | -0.0019328 |  | -56.052 | -8.4265 | -1067.5412 | -0.0021453 |  | -60 | -9.02 | -1142.7321 | -0.0023309 |  | -60 | -9.02 | -1142.7321 | -0.0024942 |  | -60 | -9.02 | -1142.7321 | -0.0026392 |  | -60 | -9.02 | -1142.7321 | -0.0027687 |  | -60 | -9.02 | -1142.7321 | -0.0028852 |  | -60 | -9.02 | -1142.7321 | -0.0029904 |  | -60 | -9.02 | -1142.7321 | -0.0030859 |  | -60 | -9.02 | -1142.7321 | -0.003173 |  | -60 | -9.02 | -1142.7321 | -0.0032528 |  | -60 | -9.02 | -1142.7321 | -0.0033262 |  | -60 | -9.02 | -1142.7321 | -0.0033938 |  | -60 | -9.02 | -1142.7321 | -0.0034564 |  | -60 | -9.02 | -1142.7321
30 |  | Steel | 30 | 0.15033 |  |  | 9.5577 | 118.5152 |  |  | 0.0011449 |  | 33.2019 | 4.9914 | 591.5512 |  | 0.000344 |  | 9.9759 | 1.4997 | 177.738 |  | -0.00027402 |  | -7.9466 | -1.1946 | -141.5824 |  | -0.00076537 |  | -22.1959 | -3.3368 | -395.459 |  | -0.0011654 |  | -33.7962 | -5.0807 | -602.1406 | -0.0014974 |  | -43.4235 | -6.528 | -773.6682 | -0.0017773 |  | -51.5417 | -7.7484 | -918.3077 | -0.0020165 |  | -58.4798 | -8.7915 | -1041.9218 | -0.0022234 |  | -60 | -9.02 | -1069.0074 | -0.0024039 |  | -60 | -9.02 | -1069.0074 | -0.002563 |  | -60 | -9.02 | -1069.0074 | -0.0027041 |  | -60 | -9.02 | -1069.0074 | -0.0028301 |  | -60 | -9.02 | -1069.0074 | -0.0029435 |  | -60 | -9.02 | -1069.0074 | -0.0030458 |  | -60 | -9.02 | -1069.0074 | -0.0031388 |  | -60 | -9.02 | -1069.0074 | -0.0032236 |  | -60 | -9.02 | -1069.0074 | -0.0033013 |  | -60 | -9.02 | -1069.0074 | -0.0033727 |  | -60 | -9.02 | -1069.0074 | -0.0034386 |  | -60 | -9.02 | -1069.0074 | -0.0034995 |  | -60 | -9.02 | -1069.0074
31 |  | Steel | 31 | 0.15033 |  |  | 8.8985 | 110.3418 |  |  | 0.00097447 |  | 28.2597 | 4.2484 | 468.7739 |  | 0.00019554 |  | 5.6707 | 0.8525 | 94.066 |  | -0.00040552 |  | -11.7602 | -1.768 | -195.0787 |  | -0.0008834 |  | -25.6187 | -3.8513 | -424.9641 |  | -0.0012724 |  | -36.9009 | -5.5474 | -612.1144 | -0.0015953 |  | -46.2642 | -6.9551 | -767.4326 | -0.0018676 |  | -54.1597 | -8.142 | -898.4037 | -0.0021003 |  | -60 | -9.02 | -995.2828 | -0.0023014 |  | -60 | -9.02 | -995.2828 | -0.002477 |  | -60 | -9.02 | -995.2828 | -0.0026317 |  | -60 | -9.02 | -995.2828 | -0.0027689 |  | -60 | -9.02 | -995.2828 | -0.0028915 |  | -60 | -9.02 | -995.2828 | -0.0030018 |  | -60 | -9.02 | -995.2828 | -0.0031013 |  | -60 | -9.02 | -995.2828 | -0.0031918 |  | -60 | -9.02 | -995.2828 | -0.0032742 |  | -60 | -9.02 | -995.2828 | -0.0033498 |  | -60 | -9.02 | -995.2828 | -0.0034192 |  | -60 | -9.02 | -995.2828 | -0.0034833 |  | -60 | -9.02 | -995.2828 | -0.0035425 |  | -60 | -9.02 | -995.2828
32 |  | Steel | 32 | 0.15033 |  |  | 8.2394 | 102.1683 |  |  | 0.00080405 |  | 23.3176 | 3.5054 | 358.1419 |  | 4.7088e-05 |  | 1.3655 | 0.20529 | 20.9738 |  | -0.00053703 |  | -15.5738 | -2.3413 | -239.2032 |  | -0.0010014 |  | -29.0415 | -4.3659 | -446.0576 |  | -0.0013795 |  | -40.0056 | -6.0142 | -614.4584 | -0.0016933 |  | -49.1048 | -7.3821 | -754.2162 | -0.0019579 |  | -56.7777 | -8.5356 | -872.066 | -0.002184 |  | -60 | -9.02 | -921.5581 | -0.0023795 |  | -60 | -9.02 | -921.5581 | -0.0025501 |  | -60 | -9.02 | -921.5581 | -0.0027004 |  | -60 | -9.02 | -921.5581 | -0.0028338 |  | -60 | -9.02 | -921.5581 | -0.002953 |  | -60 | -9.02 | -921.5581 | -0.00306 |  | -60 | -9.02 | -921.5581 | -0.0031568 |  | -60 | -9.02 | -921.5581 | -0.0032447 |  | -60 | -9.02 | -921.5581 | -0.0033249 |  | -60 | -9.02 | -921.5581 | -0.0033983 |  | -60 | -9.02 | -921.5581 | -0.0034657 |  | -60 | -9.02 | -921.5581 | -0.003528 |  | -60 | -9.02 | -921.5581 | -0.0035856 |  | -60 | -9.02 | -921.5581
33 |  | Steel | 33 | 0.15033 |  |  | 7.5802 | 93.9948 |  |  | 0.00063364 |  | 18.3754 | 2.7624 | 259.6552 |  | -0.00010137 |  | -2.9396 | -0.44192 | -41.5385 |  | -0.00066853 |  | -19.3875 | -2.9146 | -273.9556 |  | -0.0011195 |  | -32.4644 | -4.8805 | -458.7396 |  | -0.0014866 |  | -43.1103 | -6.4809 | -609.1726 | -0.0017912 |  | -51.9455 | -7.8091 | -734.0189 | -0.0020481 |  | -59.3957 | -8.9292 | -839.2946 | -0.0022677 |  | -60 | -9.02 | -847.8335 | -0.0024575 |  | -60 | -9.02 | -847.8335 | -0.0026232 |  | -60 | -9.02 | -847.8335 | -0.0027692 |  | -60 | -9.02 | -847.8335 | -0.0028987 |  | -60 | -9.02 | -847.8335 | -0.0030144 |  | -60 | -9.02 | -847.8335 | -0.0031183 |  | -60 | -9.02 | -847.8335 | -0.0032123 |  | -60 | -9.02 | -847.8335 | -0.0032976 |  | -60 | -9.02 | -847.8335 | -0.0033755 |  | -60 | -9.02 | -847.8335 | -0.0034467 |  | -60 | -9.02 | -847.8335 | -0.0035123 |  | -60 | -9.02 | -847.8335 | -0.0035727 |  | -60 | -9.02 | -847.8335 | -0.0036286 |  | -60 | -9.02 | -847.8335
34 |  | Steel | 34 | 0.15033 |  |  | 6.9211 | 85.8214 |  |  | 0.00046322 |  | 13.4333 | 2.0195 | 173.3137 |  | -0.00024982 |  | -7.2448 | -1.0891 | -93.4709 |  | -0.00080004 |  | -23.2011 | -3.4879 | -299.3361 |  | -0.0012375 |  | -35.8872 | -5.395 | -463.0099 |  | -0.0015936 |  | -46.215 | -6.9477 | -596.2572 | -0.0018892 |  | -54.7861 | -8.2362 | -706.8407 | -0.0021384 |  | -60 | -9.02 | -774.1088 | -0.0023514 |  | -60 | -9.02 | -774.1088 | -0.0025355 |  | -60 | -9.02 | -774.1088 | -0.0026963 |  | -60 | -9.02 | -774.1088 | -0.0028379 |  | -60 | -9.02 | -774.1088 | -0.0029635 |  | -60 | -9.02 | -774.1088 | -0.0030758 |  | -60 | -9.02 | -774.1088 | -0.0031766 |  | -60 | -9.02 | -774.1088 | -0.0032678 |  | -60 | -9.02 | -774.1088 | -0.0033506 |  | -60 | -9.02 | -774.1088 | -0.0034261 |  | -60 | -9.02 | -774.1088 | -0.0034952 |  | -60 | -9.02 | -774.1088 | -0.0035588 |  | -60 | -9.02 | -774.1088 | -0.0036174 |  | -60 | -9.02 | -774.1088 | -0.0036717 |  | -60 | -9.02 | -774.1088
35 |  | Steel | 35 | 0.15033 |  |  | 6.2619 | 77.6479 |  |  | 0.0002928 |  | 8.4911 | 1.2765 | 99.1176 |  | -0.00039827 |  | -11.5499 | -1.7363 | -134.8233 |  | -0.00093154 |  | -27.0147 | -4.0612 | -315.3447 |  | -0.0013555 |  | -39.31 | -5.9096 | -458.8687 |  | -0.0017007 |  | -49.3197 | -7.4144 | -575.712 | -0.0019871 |  | -57.6268 | -8.6632 | -672.6816 | -0.0022287 |  | -60 | -9.02 | -700.3842 | -0.0024351 |  | -60 | -9.02 | -700.3842 | -0.0026136 |  | -60 | -9.02 | -700.3842 | -0.0027694 |  | -60 | -9.02 | -700.3842 | -0.0029066 |  | -60 | -9.02 | -700.3842 | -0.0030284 |  | -60 | -9.02 | -700.3842 | -0.0031372 |  | -60 | -9.02 | -700.3842 | -0.0032349 |  | -60 | -9.02 | -700.3842 | -0.0033233 |  | -60 | -9.02 | -700.3842 | -0.0034035 |  | -60 | -9.02 | -700.3842 | -0.0034767 |  | -60 | -9.02 | -700.3842 | -0.0035437 |  | -60 | -9.02 | -700.3842 | -0.0036053 |  | -60 | -9.02 | -700.3842 | -0.0036621 |  | -60 | -9.02 | -700.3842 | -0.0037147 |  | -60 | -9.02 | -700.3842
36 |  | Steel | 36 | 0.15033 |  |  | 5.6028 | 69.4744 |  |  | 0.00012238 |  | 3.549 | 0.53353 | 37.0667 |  | -0.00054673 |  | -15.8551 | -2.3836 | -165.5959 |  | -0.001063 |  | -30.8283 | -4.6345 | -321.9813 |  | -0.0014735 |  | -42.7329 | -6.4242 | -446.3159 |  | -0.0018077 |  | -52.4244 | -7.8811 | -547.5371 | -0.0020851 |  | -60 | -9.02 | -626.6595 | -0.002319 |  | -60 | -9.02 | -626.6595 | -0.0025188 |  | -60 | -9.02 | -626.6595 | -0.0026916 |  | -60 | -9.02 | -626.6595 | -0.0028425 |  | -60 | -9.02 | -626.6595 | -0.0029753 |  | -60 | -9.02 | -626.6595 | -0.0030932 |  | -60 | -9.02 | -626.6595 | -0.0031986 |  | -60 | -9.02 | -626.6595 | -0.0032932 |  | -60 | -9.02 | -626.6595 | -0.0033788 |  | -60 | -9.02 | -626.6595 | -0.0034564 |  | -60 | -9.02 | -626.6595 | -0.0035273 |  | -60 | -9.02 | -626.6595 | -0.0035922 |  | -60 | -9.02 | -626.6595 | -0.0036518 |  | -60 | -9.02 | -626.6595 | -0.0037068 |  | -60 | -9.02 | -626.6595 | -0.0037577 |  | -60 | -9.02 | -626.6595
37 |  | Steel | 37 | 0.15033 |  |  | 4.9436 | 61.301 |  |  | -4.804e-05 |  | -1.3932 | -0.20944 | -12.8389 |  | -0.00069518 |  | -20.1603 | -3.0308 | -185.7887 |  | -0.0011946 |  | -34.642 | -5.2078 | -319.2459 |  | -0.0015916 |  | -46.1557 | -6.9387 | -425.3516 |  | -0.0019148 |  | -55.529 | -8.3479 | -511.7324 | -0.002183 |  | -60 | -9.02 | -552.9349 | -0.0024092 |  | -60 | -9.02 | -552.9349 | -0.0026025 |  | -60 | -9.02 | -552.9349 | -0.0027697 |  | -60 | -9.02 | -552.9349 | -0.0029156 |  | -60 | -9.02 | -552.9349 | -0.0030441 |  | -60 | -9.02 | -552.9349 | -0.0031581 |  | -60 | -9.02 | -552.9349 | -0.00326 |  | -60 | -9.02 | -552.9349 | -0.0033515 |  | -60 | -9.02 | -552.9349 | -0.0034342 |  | -60 | -9.02 | -552.9349 | -0.0035094 |  | -60 | -9.02 | -552.9349 | -0.0035779 |  | -60 | -9.02 | -552.9349 | -0.0036407 |  | -60 | -9.02 | -552.9349 | -0.0036984 |  | -60 | -9.02 | -552.9349 | -0.0037516 |  | -60 | -9.02 | -552.9349 | -0.0038008 |  | -60 | -9.02 | -552.9349
38 |  | Steel | 38 | 0.15033 |  |  | 4.2845 | 53.1275 |  |  | -0.00021846 |  | -6.3353 | -0.95241 | -50.5992 |  | -0.00084364 |  | -24.4654 | -3.678 | -195.4015 |  | -0.0013261 |  | -38.4556 | -5.7812 | -307.1387 |  | -0.0017096 |  | -49.5785 | -7.4533 | -395.9756 |  | -0.0020219 |  | -58.6337 | -8.8146 | -468.298 | -0.002281 |  | -60 | -9.02 | -479.2102 | -0.0024995 |  | -60 | -9.02 | -479.2102 | -0.0026863 |  | -60 | -9.02 | -479.2102 | -0.0028477 |  | -60 | -9.02 | -479.2102 | -0.0029887 |  | -60 | -9.02 | -479.2102 | -0.0031128 |  | -60 | -9.02 | -479.2102 | -0.0032229 |  | -60 | -9.02 | -479.2102 | -0.0033214 |  | -60 | -9.02 | -479.2102 | -0.0034098 |  | -60 | -9.02 | -479.2102 | -0.0034897 |  | -60 | -9.02 | -479.2102 | -0.0035623 |  | -60 | -9.02 | -479.2102 | -0.0036285 |  | -60 | -9.02 | -479.2102 | -0.0036891 |  | -60 | -9.02 | -479.2102 | -0.0037449 |  | -60 | -9.02 | -479.2102 | -0.0037963 |  | -60 | -9.02 | -479.2102 | -0.0038438 |  | -60 | -9.02 | -479.2102
39 |  | Steel | 39 | 0.15033 |  |  | 3.6253 | 44.9541 |  |  | -0.00038888 |  | -11.2775 | -1.6954 | -76.2142 |  | -0.00099209 |  | -28.7706 | -4.3252 | -194.4344 |  | -0.0014576 |  | -42.2692 | -6.3545 | -285.6594 |  | -0.0018276 |  | -53.0014 | -7.9679 | -358.1881 |  | -0.0021289 |  | -60 | -9.02 | -405.4856 | -0.0023789 |  | -60 | -9.02 | -405.4856 | -0.0025898 |  | -60 | -9.02 | -405.4856 | -0.00277 |  | -60 | -9.02 | -405.4856 | -0.0029257 |  | -60 | -9.02 | -405.4856 | -0.0030618 |  | -60 | -9.02 | -405.4856 | -0.0031815 |  | -60 | -9.02 | -405.4856 | -0.0032878 |  | -60 | -9.02 | -405.4856 | -0.0033828 |  | -60 | -9.02 | -405.4856 | -0.0034681 |  | -60 | -9.02 | -405.4856 | -0.0035452 |  | -60 | -9.02 | -405.4856 | -0.0036152 |  | -60 | -9.02 | -405.4856 | -0.0036791 |  | -60 | -9.02 | -405.4856 | -0.0037376 |  | -60 | -9.02 | -405.4856 | -0.0037914 |  | -60 | -9.02 | -405.4856 | -0.003841 |  | -60 | -9.02 | -405.4856 | -0.0038869 |  | -60 | -9.02 | -405.4856
40 |  | Steel | 40 | 0.15033 |  |  | 2.9662 | 36.7806 |  |  | -0.0005593 |  | -16.2196 | -2.4384 | -89.684 |  | -0.0011405 |  | -33.0758 | -4.9724 | -182.8875 |  | -0.0015891 |  | -46.0829 | -6.9278 | -254.8082 |  | -0.0019457 |  | -56.4242 | -8.4824 | -311.9891 |  | -0.002236 |  | -60 | -9.02 | -331.7609 | -0.0024769 |  | -60 | -9.02 | -331.7609 | -0.0026801 |  | -60 | -9.02 | -331.7609 | -0.0028537 |  | -60 | -9.02 | -331.7609 | -0.0030038 |  | -60 | -9.02 | -331.7609 | -0.0031348 |  | -60 | -9.02 | -331.7609 | -0.0032503 |  | -60 | -9.02 | -331.7609 | -0.0033527 |  | -60 | -9.02 | -331.7609 | -0.0034442 |  | -60 | -9.02 | -331.7609 | -0.0035264 |  | -60 | -9.02 | -331.7609 | -0.0036007 |  | -60 | -9.02 | -331.7609 | -0.0036682 |  | -60 | -9.02 | -331.7609 | -0.0037297 |  | -60 | -9.02 | -331.7609 | -0.0037861 |  | -60 | -9.02 | -331.7609 | -0.0038379 |  | -60 | -9.02 | -331.7609 | -0.0038857 |  | -60 | -9.02 | -331.7609 | -0.0039299 |  | -60 | -9.02 | -331.7609
41 |  | Steel | 41 | 0.15033 |  |  | 2.307 | 28.6071 |  |  | -0.00072972 |  | -21.1618 | -3.1813 | -91.0085 |  | -0.001289 |  | -37.3809 | -5.6196 | -160.7606 |  | -0.0017206 |  | -49.8965 | -7.5011 | -214.5851 |  | -0.0020637 |  | -59.847 | -8.997 | -257.3784 |  | -0.002343 |  | -60 | -9.02 | -258.0363 | -0.0025749 |  | -60 | -9.02 | -258.0363 | -0.0027703 |  | -60 | -9.02 | -258.0363 | -0.0029374 |  | -60 | -9.02 | -258.0363 | -0.0030818 |  | -60 | -9.02 | -258.0363 | -0.0032079 |  | -60 | -9.02 | -258.0363 | -0.003319 |  | -60 | -9.02 | -258.0363 | -0.0034175 |  | -60 | -9.02 | -258.0363 | -0.0035056 |  | -60 | -9.02 | -258.0363 | -0.0035847 |  | -60 | -9.02 | -258.0363 | -0.0036562 |  | -60 | -9.02 | -258.0363 | -0.0037211 |  | -60 | -9.02 | -258.0363 | -0.0037803 |  | -60 | -9.02 | -258.0363 | -0.0038346 |  | -60 | -9.02 | -258.0363 | -0.0038844 |  | -60 | -9.02 | -258.0363 | -0.0039304 |  | -60 | -9.02 | -258.0363 | -0.003973 |  | -60 | -9.02 | -258.0363
42 |  | Steel | 42 | 0.15033 |  |  | 1.6479 | 20.4337 |  |  | -0.00090014 |  | -26.1039 | -3.9243 | -80.1876 |  | -0.0014375 |  | -41.6861 | -6.2668 | -128.0539 |  | -0.0018521 |  | -53.7101 | -8.0744 | -164.99 |  | -0.0021817 |  | -60 | -9.02 | -184.3116 |  | -0.0024501 |  | -60 | -9.02 | -184.3116 | -0.0026728 |  | -60 | -9.02 | -184.3116 | -0.0028606 |  | -60 | -9.02 | -184.3116 | -0.0030211 |  | -60 | -9.02 | -184.3116 | -0.0031599 |  | -60 | -9.02 | -184.3116 | -0.003281 |  | -60 | -9.02 | -184.3116 | -0.0033877 |  | -60 | -9.02 | -184.3116 | -0.0034824 |  | -60 | -9.02 | -184.3116 | -0.003567 |  | -60 | -9.02 | -184.3116 | -0.003643 |  | -60 | -9.02 | -184.3116 | -0.0037117 |  | -60 | -9.02 | -184.3116 | -0.0037741 |  | -60 | -9.02 | -184.3116 | -0.0038309 |  | -60 | -9.02 | -184.3116 | -0.0038831 |  | -60 | -9.02 | -184.3116 | -0.003931 |  | -60 | -9.02 | -184.3116 | -0.0039751 |  | -60 | -9.02 | -184.3116 | -0.004016 |  | -60 | -9.02 | -184.3116
43 |  | Steel | 43 | 0.15033 |  |  | 0.98873 | 12.2602 |  |  | -0.0010706 |  | -31.0461 | -4.6673 | -57.2215 |  | -0.0015859 |  | -45.9913 | -6.914 | -84.7672 |  | -0.0019836 |  | -57.5238 | -8.6477 | -106.023 |  | -0.0022997 |  | -60 | -9.02 | -110.587 |  | -0.0025571 |  | -60 | -9.02 | -110.587 | -0.0027708 |  | -60 | -9.02 | -110.587 | -0.0029509 |  | -60 | -9.02 | -110.587 | -0.0031048 |  | -60 | -9.02 | -110.587 | -0.0032379 |  | -60 | -9.02 | -110.587 | -0.0033541 |  | -60 | -9.02 | -110.587 | -0.0034564 |  | -60 | -9.02 | -110.587 | -0.0035472 |  | -60 | -9.02 | -110.587 | -0.0036284 |  | -60 | -9.02 | -110.587 | -0.0037013 |  | -60 | -9.02 | -110.587 | -0.0037672 |  | -60 | -9.02 | -110.587 | -0.003827 |  | -60 | -9.02 | -110.587 | -0.0038816 |  | -60 | -9.02 | -110.587 | -0.0039315 |  | -60 | -9.02 | -110.587 | -0.0039775 |  | -60 | -9.02 | -110.587 | -0.0040199 |  | -60 | -9.02 | -110.587 | -0.0040591 |  | -60 | -9.02 | -110.587
44 |  | Steel | 44 | 0.15033 |  |  | 0.32958 | 4.0867 |  |  | -0.001241 |  | -35.9882 | -5.4102 | -22.1102 |  | -0.0017344 |  | -50.2964 | -7.5612 | -30.9007 |  | -0.0021151 |  | -60 | -9.02 | -36.8623 |  | -0.0024178 |  | -60 | -9.02 | -36.8623 |  | -0.0026642 |  | -60 | -9.02 | -36.8623 | -0.0028687 |  | -60 | -9.02 | -36.8623 | -0.0030412 |  | -60 | -9.02 | -36.8623 | -0.0031885 |  | -60 | -9.02 | -36.8623 | -0.003316 |  | -60 | -9.02 | -36.8623 | -0.0034272 |  | -60 | -9.02 | -36.8623 | -0.0035252 |  | -60 | -9.02 | -36.8623 | -0.0036121 |  | -60 | -9.02 | -36.8623 | -0.0036898 |  | -60 | -9.02 | -36.8623 | -0.0037596 |  | -60 | -9.02 | -36.8623 | -0.0038226 |  | -60 | -9.02 | -36.8623 | -0.0038799 |  | -60 | -9.02 | -36.8623 | -0.0039322 |  | -60 | -9.02 | -36.8623 | -0.00398 |  | -60 | -9.02 | -36.8623 | -0.004024 |  | -60 | -9.02 | -36.8623 | -0.0040646 |  | -60 | -9.02 | -36.8623 | -0.0041021 |  | -60 | -9.02 | -36.8623
45 |  | Steel | 45 | 0.15033 |  |  | -0.32958 | -4.0867 |  |  | -0.0014114 |  | -40.9304 | -6.1532 | 25.1465 |  | -0.0018828 |  | -54.6016 | -8.2084 | 33.5457 |  | -0.0022466 |  | -60 | -9.02 | 36.8623 |  | -0.0025358 |  | -60 | -9.02 | 36.8623 |  | -0.0027713 |  | -60 | -9.02 | 36.8623 | -0.0029667 |  | -60 | -9.02 | 36.8623 | -0.0031314 |  | -60 | -9.02 | 36.8623 | -0.0032723 |  | -60 | -9.02 | 36.8623 | -0.003394 |  | -60 | -9.02 | 36.8623 | -0.0035003 |  | -60 | -9.02 | 36.8623 | -0.0035939 |  | -60 | -9.02 | 36.8623 | -0.003677 |  | -60 | -9.02 | 36.8623 | -0.0037512 |  | -60 | -9.02 | 36.8623 | -0.0038179 |  | -60 | -9.02 | 36.8623 | -0.0038781 |  | -60 | -9.02 | 36.8623 | -0.0039329 |  | -60 | -9.02 | 36.8623 | -0.0039828 |  | -60 | -9.02 | 36.8623 | -0.0040285 |  | -60 | -9.02 | 36.8623 | -0.0040705 |  | -60 | -9.02 | 36.8623 | -0.0041093 |  | -60 | -9.02 | 36.8623 | -0.0041451 |  | -60 | -9.02 | 36.8623
46 |  | Steel | 46 | 0.15033 |  |  | -0.98873 | -12.2602 |  |  | -0.0015818 |  | -45.8725 | -6.8962 | 84.5484 |  | -0.0020313 |  | -58.9068 | -8.8556 | 108.572 |  | -0.0023781 |  | -60 | -9.02 | 110.587 |  | -0.0026538 |  | -60 | -9.02 | 110.587 |  | -0.0028783 |  | -60 | -9.02 | 110.587 | -0.0030646 |  | -60 | -9.02 | 110.587 | -0.0032217 |  | -60 | -9.02 | 110.587 | -0.003356 |  | -60 | -9.02 | 110.587 | -0.003472 |  | -60 | -9.02 | 110.587 | -0.0035734 |  | -60 | -9.02 | 110.587 | -0.0036626 |  | -60 | -9.02 | 110.587 | -0.0037418 |  | -60 | -9.02 | 110.587 | -0.0038126 |  | -60 | -9.02 | 110.587 | -0.0038762 |  | -60 | -9.02 | 110.587 | -0.0039336 |  | -60 | -9.02 | 110.587 | -0.0039858 |  | -60 | -9.02 | 110.587 | -0.0040334 |  | -60 | -9.02 | 110.587 | -0.004077 |  | -60 | -9.02 | 110.587 | -0.004117 |  | -60 | -9.02 | 110.587 | -0.004154 |  | -60 | -9.02 | 110.587 | -0.0041882 |  | -60 | -9.02 | 110.587
47 |  | Steel | 47 | 0.15033 |  |  | -1.6479 | -20.4337 |  |  | -0.0017522 |  | -50.8147 | -7.6391 | 156.0957 |  | -0.0021797 |  | -60 | -9.02 | 184.3116 |  | -0.0025096 |  | -60 | -9.02 | 184.3116 |  | -0.0027719 |  | -60 | -9.02 | 184.3116 |  | -0.0029854 |  | -60 | -9.02 | 184.3116 | -0.0031626 |  | -60 | -9.02 | 184.3116 | -0.003312 |  | -60 | -9.02 | 184.3116 | -0.0034397 |  | -60 | -9.02 | 184.3116 | -0.0035501 |  | -60 | -9.02 | 184.3116 | -0.0036465 |  | -60 | -9.02 | 184.3116 | -0.0037314 |  | -60 | -9.02 | 184.3116 | -0.0038067 |  | -60 | -9.02 | 184.3116 | -0.003874 |  | -60 | -9.02 | 184.3116 | -0.0039344 |  | -60 | -9.02 | 184.3116 | -0.0039891 |  | -60 | -9.02 | 184.3116 | -0.0040387 |  | -60 | -9.02 | 184.3116 | -0.004084 |  | -60 | -9.02 | 184.3116 | -0.0041255 |  | -60 | -9.02 | 184.3116 | -0.0041636 |  | -60 | -9.02 | 184.3116 | -0.0041987 |  | -60 | -9.02 | 184.3116 | -0.0042312 |  | -60 | -9.02 | 184.3116
48 |  | Steel | 48 | 0.15033 |  |  | -2.307 | -28.6071 |  |  | -0.0019226 |  | -55.7568 | -8.3821 | 239.7882 |  | -0.0023282 |  | -60 | -9.02 | 258.0363 |  | -0.0026411 |  | -60 | -9.02 | 258.0363 |  | -0.0028899 |  | -60 | -9.02 | 258.0363 |  | -0.0030924 |  | -60 | -9.02 | 258.0363 | -0.0032605 |  | -60 | -9.02 | 258.0363 | -0.0034023 |  | -60 | -9.02 | 258.0363 | -0.0035234 |  | -60 | -9.02 | 258.0363 | -0.0036281 |  | -60 | -9.02 | 258.0363 | -0.0037196 |  | -60 | -9.02 | 258.0363 | -0.0038001 |  | -60 | -9.02 | 258.0363 | -0.0038715 |  | -60 | -9.02 | 258.0363 | -0.0039354 |  | -60 | -9.02 | 258.0363 | -0.0039927 |  | -60 | -9.02 | 258.0363 | -0.0040446 |  | -60 | -9.02 | 258.0363 | -0.0040917 |  | -60 | -9.02 | 258.0363 | -0.0041346 |  | -60 | -9.02 | 258.0363 | -0.0041739 |  | -60 | -9.02 | 258.0363 | -0.0042101 |  | -60 | -9.02 | 258.0363 | -0.0042434 |  | -60 | -9.02 | 258.0363 | -0.0042743 |  | -60 | -9.02 | 258.0363
49 |  | Steel | 49 | 0.15033 |  |  | -2.9662 | -36.7806 |  |  | -0.0020931 |  | -60 | -9.02 | 331.7609 |  | -0.0024766 |  | -60 | -9.02 | 331.7609 |  | -0.0027726 |  | -60 | -9.02 | 331.7609 |  | -0.0030079 |  | -60 | -9.02 | 331.7609 |  | -0.0031995 |  | -60 | -9.02 | 331.7609 | -0.0033585 |  | -60 | -9.02 | 331.7609 | -0.0034925 |  | -60 | -9.02 | 331.7609 | -0.0036071 |  | -60 | -9.02 | 331.7609 | -0.0037062 |  | -60 | -9.02 | 331.7609 | -0.0037927 |  | -60 | -9.02 | 331.7609 | -0.0038688 |  | -60 | -9.02 | 331.7609 | -0.0039364 |  | -60 | -9.02 | 331.7609 | -0.0039968 |  | -60 | -9.02 | 331.7609 | -0.004051 |  | -60 | -9.02 | 331.7609 | -0.0041001 |  | -60 | -9.02 | 331.7609 | -0.0041446 |  | -60 | -9.02 | 331.7609 | -0.0041852 |  | -60 | -9.02 | 331.7609 | -0.0042224 |  | -60 | -9.02 | 331.7609 | -0.0042566 |  | -60 | -9.02 | 331.7609 | -0.0042881 |  | -60 | -9.02 | 331.7609 | -0.0043173 |  | -60 | -9.02 | 331.7609
50 |  | Steel | 50 | 0.15033 |  |  | -3.6253 | -44.9541 |  |  | -0.0022635 |  | -60 | -9.02 | 405.4856 |  | -0.0026251 |  | -60 | -9.02 | 405.4856 |  | -0.0029041 |  | -60 | -9.02 | 405.4856 |  | -0.0031259 |  | -60 | -9.02 | 405.4856 |  | -0.0033066 |  | -60 | -9.02 | 405.4856 | -0.0034564 |  | -60 | -9.02 | 405.4856 | -0.0035828 |  | -60 | -9.02 | 405.4856 | -0.0036908 |  | -60 | -9.02 | 405.4856 | -0.0037842 |  | -60 | -9.02 | 405.4856 | -0.0038657 |  | -60 | -9.02 | 405.4856 | -0.0039375 |  | -60 | -9.02 | 405.4856 | -0.0040012 |  | -60 | -9.02 | 405.4856 | -0.0040582 |  | -60 | -9.02 | 405.4856 | -0.0041093 |  | -60 | -9.02 | 405.4856 | -0.0041556 |  | -60 | -9.02 | 405.4856 | -0.0041975 |  | -60 | -9.02 | 405.4856 | -0.0042358 |  | -60 | -9.02 | 405.4856 | -0.0042709 |  | -60 | -9.02 | 405.4856 | -0.0043031 |  | -60 | -9.02 | 405.4856 | -0.0043329 |  | -60 | -9.02 | 405.4856 | -0.0043604 |  | -60 | -9.02 | 405.4856
51 |  | Steel | 51 | 0.15033 |  |  | -4.2845 | -53.1275 |  |  | -0.0024339 |  | -60 | -9.02 | 479.2102 |  | -0.0027735 |  | -60 | -9.02 | 479.2102 |  | -0.0030356 |  | -60 | -9.02 | 479.2102 |  | -0.003244 |  | -60 | -9.02 | 479.2102 |  | -0.0034136 |  | -60 | -9.02 | 479.2102 | -0.0035544 |  | -60 | -9.02 | 479.2102 | -0.0036731 |  | -60 | -9.02 | 479.2102 | -0.0037746 |  | -60 | -9.02 | 479.2102 | -0.0038623 |  | -60 | -9.02 | 479.2102 | -0.0039388 |  | -60 | -9.02 | 479.2102 | -0.0040063 |  | -60 | -9.02 | 479.2102 | -0.0040661 |  | -60 | -9.02 | 479.2102 | -0.0041196 |  | -60 | -9.02 | 479.2102 | -0.0041676 |  | -60 | -9.02 | 479.2102 | -0.004211 |  | -60 | -9.02 | 479.2102 | -0.0042505 |  | -60 | -9.02 | 479.2102 | -0.0042864 |  | -60 | -9.02 | 479.2102 | -0.0043194 |  | -60 | -9.02 | 479.2102 | -0.0043496 |  | -60 | -9.02 | 479.2102 | -0.0043776 |  | -60 | -9.02 | 479.2102 | -0.0044034 |  | -60 | -9.02 | 479.2102
52 |  | Steel | 52 | 0.15033 |  |  | -4.9436 | -61.301 |  |  | -0.0026043 |  | -60 | -9.02 | 552.9349 |  | -0.002922 |  | -60 | -9.02 | 552.9349 |  | -0.0031671 |  | -60 | -9.02 | 552.9349 |  | -0.003362 |  | -60 | -9.02 | 552.9349 |  | -0.0035207 |  | -60 | -9.02 | 552.9349 | -0.0036523 |  | -60 | -9.02 | 552.9349 | -0.0037634 |  | -60 | -9.02 | 552.9349 | -0.0038583 |  | -60 | -9.02 | 552.9349 | -0.0039403 |  | -60 | -9.02 | 552.9349 | -0.0040119 |  | -60 | -9.02 | 552.9349 | -0.004075 |  | -60 | -9.02 | 552.9349 | -0.004131 |  | -60 | -9.02 | 552.9349 | -0.004181 |  | -60 | -9.02 | 552.9349 | -0.0042259 |  | -60 | -9.02 | 552.9349 | -0.0042665 |  | -60 | -9.02 | 552.9349 | -0.0043034 |  | -60 | -9.02 | 552.9349 | -0.004337 |  | -60 | -9.02 | 552.9349 | -0.0043678 |  | -60 | -9.02 | 552.9349 | -0.0043962 |  | -60 | -9.02 | 552.9349 | -0.0044223 |  | -60 | -9.02 | 552.9349 | -0.0044465 |  | -60 | -9.02 | 552.9349
53 |  | Steel | 53 | 0.15033 |  |  | -5.6028 | -69.4744 |  |  | -0.0027747 |  | -60 | -9.02 | 626.6595 |  | -0.0030704 |  | -60 | -9.02 | 626.6595 |  | -0.0032986 |  | -60 | -9.02 | 626.6595 |  | -0.00348 |  | -60 | -9.02 | 626.6595 |  | -0.0036277 |  | -60 | -9.02 | 626.6595 | -0.0037503 |  | -60 | -9.02 | 626.6595 | -0.0038536 |  | -60 | -9.02 | 626.6595 | -0.003942 |  | -60 | -9.02 | 626.6595 | -0.0040183 |  | -60 | -9.02 | 626.6595 | -0.004085 |  | -60 | -9.02 | 626.6595 | -0.0041437 |  | -60 | -9.02 | 626.6595 | -0.0041958 |  | -60 | -9.02 | 626.6595 | -0.0042424 |  | -60 | -9.02 | 626.6595 | -0.0042842 |  | -60 | -9.02 | 626.6595 | -0.004322 |  | -60 | -9.02 | 626.6595 | -0.0043563 |  | -60 | -9.02 | 626.6595 | -0.0043877 |  | -60 | -9.02 | 626.6595 | -0.0044163 |  | -60 | -9.02 | 626.6595 | -0.0044427 |  | -60 | -9.02 | 626.6595 | -0.004467 |  | -60 | -9.02 | 626.6595 | -0.0044895 |  | -60 | -9.02 | 626.6595
54 |  | Steel | 54 | 0.15033 |  |  | -6.2619 | -77.6479 |  |  | -0.0029452 |  | -60 | -9.02 | 700.3842 |  | -0.0032189 |  | -60 | -9.02 | 700.3842 |  | -0.0034301 |  | -60 | -9.02 | 700.3842 |  | -0.0035981 |  | -60 | -9.02 | 700.3842 |  | -0.0037348 |  | -60 | -9.02 | 700.3842 | -0.0038482 |  | -60 | -9.02 | 700.3842 | -0.0039439 |  | -60 | -9.02 | 700.3842 | -0.0040257 |  | -60 | -9.02 | 700.3842 | -0.0040964 |  | -60 | -9.02 | 700.3842 | -0.0041581 |  | -60 | -9.02 | 700.3842 | -0.0042125 |  | -60 | -9.02 | 700.3842 | -0.0042607 |  | -60 | -9.02 | 700.3842 | -0.0043038 |  | -60 | -9.02 | 700.3842 | -0.0043425 |  | -60 | -9.02 | 700.3842 | -0.0043775 |  | -60 | -9.02 | 700.3842 | -0.0044093 |  | -60 | -9.02 | 700.3842 | -0.0044383 |  | -60 | -9.02 | 700.3842 | -0.0044648 |  | -60 | -9.02 | 700.3842 | -0.0044892 |  | -60 | -9.02 | 700.3842 | -0.0045117 |  | -60 | -9.02 | 700.3842 | -0.0045325 |  | -60 | -9.02 | 700.3842
55 |  | Steel | 55 | 0.15033 |  |  | -6.9211 | -85.8214 |  |  | -0.0031156 |  | -60 | -9.02 | 774.1088 |  | -0.0033674 |  | -60 | -9.02 | 774.1088 |  | -0.0035616 |  | -60 | -9.02 | 774.1088 |  | -0.0037161 |  | -60 | -9.02 | 774.1088 |  | -0.0038418 |  | -60 | -9.02 | 774.1088 | -0.0039462 |  | -60 | -9.02 | 774.1088 | -0.0040342 |  | -60 | -9.02 | 774.1088 | -0.0041094 |  | -60 | -9.02 | 774.1088 | -0.0041744 |  | -60 | -9.02 | 774.1088 | -0.0042312 |  | -60 | -9.02 | 774.1088 | -0.0042812 |  | -60 | -9.02 | 774.1088 | -0.0043255 |  | -60 | -9.02 | 774.1088 | -0.0043652 |  | -60 | -9.02 | 774.1088 | -0.0044008 |  | -60 | -9.02 | 774.1088 | -0.004433 |  | -60 | -9.02 | 774.1088 | -0.0044622 |  | -60 | -9.02 | 774.1088 | -0.0044889 |  | -60 | -9.02 | 774.1088 | -0.0045133 |  | -60 | -9.02 | 774.1088 | -0.0045357 |  | -60 | -9.02 | 774.1088 | -0.0045564 |  | -60 | -9.02 | 774.1088 | -0.0045756 |  | -60 | -9.02 | 774.1088
56 |  | Steel | 56 | 0.15033 |  |  | -7.5802 | -93.9948 |  |  | -0.003286 |  | -60 | -9.02 | 847.8335 |  | -0.0035158 |  | -60 | -9.02 | 847.8335 |  | -0.0036931 |  | -60 | -9.02 | 847.8335 |  | -0.0038341 |  | -60 | -9.02 | 847.8335 |  | -0.0039489 |  | -60 | -9.02 | 847.8335 | -0.0040442 |  | -60 | -9.02 | 847.8335 | -0.0041245 |  | -60 | -9.02 | 847.8335 | -0.0041931 |  | -60 | -9.02 | 847.8335 | -0.0042525 |  | -60 | -9.02 | 847.8335 | -0.0043043 |  | -60 | -9.02 | 847.8335 | -0.0043499 |  | -60 | -9.02 | 847.8335 | -0.0043904 |  | -60 | -9.02 | 847.8335 | -0.0044266 |  | -60 | -9.02 | 847.8335 | -0.0044591 |  | -60 | -9.02 | 847.8335 | -0.0044885 |  | -60 | -9.02 | 847.8335 | -0.0045151 |  | -60 | -9.02 | 847.8335 | -0.0045395 |  | -60 | -9.02 | 847.8335 | -0.0045618 |  | -60 | -9.02 | 847.8335 | -0.0045823 |  | -60 | -9.02 | 847.8335 | -0.0046011 |  | -60 | -9.02 | 847.8335 | -0.0046186 |  | -60 | -9.02 | 847.8335
57 |  | Steel | 57 | 0.15033 |  |  | -8.2394 | -102.1683 |  |  | -0.0034564 |  | -60 | -9.02 | 921.5581 |  | -0.0036643 |  | -60 | -9.02 | 921.5581 |  | -0.0038246 |  | -60 | -9.02 | 921.5581 |  | -0.0039522 |  | -60 | -9.02 | 921.5581 |  | -0.004056 |  | -60 | -9.02 | 921.5581 | -0.0041421 |  | -60 | -9.02 | 921.5581 | -0.0042148 |  | -60 | -9.02 | 921.5581 | -0.0042768 |  | -60 | -9.02 | 921.5581 | -0.0043305 |  | -60 | -9.02 | 921.5581 | -0.0043774 |  | -60 | -9.02 | 921.5581 | -0.0044186 |  | -60 | -9.02 | 921.5581 | -0.0044553 |  | -60 | -9.02 | 921.5581 | -0.004488 |  | -60 | -9.02 | 921.5581 | -0.0045174 |  | -60 | -9.02 | 921.5581 | -0.004544 |  | -60 | -9.02 | 921.5581 | -0.0045681 |  | -60 | -9.02 | 921.5581 | -0.0045901 |  | -60 | -9.02 | 921.5581 | -0.0046102 |  | -60 | -9.02 | 921.5581 | -0.0046288 |  | -60 | -9.02 | 921.5581 | -0.0046459 |  | -60 | -9.02 | 921.5581 | -0.0046617 |  | -60 | -9.02 | 921.5581
58 |  | Steel | 58 | 0.15033 |  |  | -8.8985 | -110.3418 |  |  | -0.0036268 |  | -60 | -9.02 | 995.2828 |  | -0.0038127 |  | -60 | -9.02 | 995.2828 |  | -0.0039561 |  | -60 | -9.02 | 995.2828 |  | -0.0040702 |  | -60 | -9.02 | 995.2828 |  | -0.004163 |  | -60 | -9.02 | 995.2828 | -0.0042401 |  | -60 | -9.02 | 995.2828 | -0.004305 |  | -60 | -9.02 | 995.2828 | -0.0043606 |  | -60 | -9.02 | 995.2828 | -0.0044086 |  | -60 | -9.02 | 995.2828 | -0.0044505 |  | -60 | -9.02 | 995.2828 | -0.0044874 |  | -60 | -9.02 | 995.2828 | -0.0045201 |  | -60 | -9.02 | 995.2828 | -0.0045494 |  | -60 | -9.02 | 995.2828 | -0.0045757 |  | -60 | -9.02 | 995.2828 | -0.0045994 |  | -60 | -9.02 | 995.2828 | -0.004621 |  | -60 | -9.02 | 995.2828 | -0.0046407 |  | -60 | -9.02 | 995.2828 | -0.0046587 |  | -60 | -9.02 | 995.2828 | -0.0046753 |  | -60 | -9.02 | 995.2828 | -0.0046906 |  | -60 | -9.02 | 995.2828 | -0.0047047 |  | -60 | -9.02 | 995.2828
59 |  | Steel | 59 | 0.15033 |  |  | -9.5577 | -118.5152 |  |  | -0.0037973 |  | -60 | -9.02 | 1069.0074 |  | -0.0039612 |  | -60 | -9.02 | 1069.0074 |  | -0.0040876 |  | -60 | -9.02 | 1069.0074 |  | -0.0041882 |  | -60 | -9.02 | 1069.0074 |  | -0.0042701 |  | -60 | -9.02 | 1069.0074 | -0.004338 |  | -60 | -9.02 | 1069.0074 | -0.0043953 |  | -60 | -9.02 | 1069.0074 | -0.0044443 |  | -60 | -9.02 | 1069.0074 | -0.0044866 |  | -60 | -9.02 | 1069.0074 | -0.0045236 |  | -60 | -9.02 | 1069.0074 | -0.0045561 |  | -60 | -9.02 | 1069.0074 | -0.004585 |  | -60 | -9.02 | 1069.0074 | -0.0046108 |  | -60 | -9.02 | 1069.0074 | -0.004634 |  | -60 | -9.02 | 1069.0074 | -0.0046549 |  | -60 | -9.02 | 1069.0074 | -0.004674 |  | -60 | -9.02 | 1069.0074 | -0.0046913 |  | -60 | -9.02 | 1069.0074 | -0.0047072 |  | -60 | -9.02 | 1069.0074 | -0.0047218 |  | -60 | -9.02 | 1069.0074 | -0.0047353 |  | -60 | -9.02 | 1069.0074 | -0.0047478 |  | -60 | -9.02 | 1069.0074
60 |  | Steel | 60 | 0.15033 |  |  | -10.2168 | -126.6887 |  |  | -0.0039677 |  | -60 | -9.02 | 1142.7321 |  | -0.0041096 |  | -60 | -9.02 | 1142.7321 |  | -0.0042192 |  | -60 | -9.02 | 1142.7321 |  | -0.0043062 |  | -60 | -9.02 | 1142.7321 |  | -0.0043771 |  | -60 | -9.02 | 1142.7321 | -0.004436 |  | -60 | -9.02 | 1142.7321 | -0.0044856 |  | -60 | -9.02 | 1142.7321 | -0.004528 |  | -60 | -9.02 | 1142.7321 | -0.0045646 |  | -60 | -9.02 | 1142.7321 | -0.0045966 |  | -60 | -9.02 | 1142.7321 | -0.0046248 |  | -60 | -9.02 | 1142.7321 | -0.0046498 |  | -60 | -9.02 | 1142.7321 | -0.0046722 |  | -60 | -9.02 | 1142.7321 | -0.0046923 |  | -60 | -9.02 | 1142.7321 | -0.0047104 |  | -60 | -9.02 | 1142.7321 | -0.0047269 |  | -60 | -9.02 | 1142.7321 | -0.0047419 |  | -60 | -9.02 | 1142.7321 | -0.0047557 |  | -60 | -9.02 | 1142.7321 | -0.0047683 |  | -60 | -9.02 | 1142.7321 | -0.00478 |  | -60 | -9.02 | 1142.7321 | -0.0047908 |  | -60 | -9.02 | 1142.7321
61 |  | Steel | 61 | 0.15033 |  |  | -10.876 | -134.8622 |  |  | -0.0041381 |  | -60 | -9.02 | 1216.4567 |  | -0.0042581 |  | -60 | -9.02 | 1216.4567 |  | -0.0043507 |  | -60 | -9.02 | 1216.4567 |  | -0.0044243 |  | -60 | -9.02 | 1216.4567 |  | -0.0044842 |  | -60 | -9.02 | 1216.4567 | -0.0045339 |  | -60 | -9.02 | 1216.4567 | -0.0045759 |  | -60 | -9.02 | 1216.4567 | -0.0046117 |  | -60 | -9.02 | 1216.4567 | -0.0046427 |  | -60 | -9.02 | 1216.4567 | -0.0046697 |  | -60 | -9.02 | 1216.4567 | -0.0046936 |  | -60 | -9.02 | 1216.4567 | -0.0047147 |  | -60 | -9.02 | 1216.4567 | -0.0047336 |  | -60 | -9.02 | 1216.4567 | -0.0047506 |  | -60 | -9.02 | 1216.4567 | -0.0047659 |  | -60 | -9.02 | 1216.4567 | -0.0047798 |  | -60 | -9.02 | 1216.4567 | -0.0047925 |  | -60 | -9.02 | 1216.4567 | -0.0048042 |  | -60 | -9.02 | 1216.4567 | -0.0048149 |  | -60 | -9.02 | 1216.4567 | -0.0048247 |  | -60 | -9.02 | 1216.4567 | -0.0048338 |  | -60 | -9.02 | 1216.4567
62 |  | Steel | 62 | 0.15033 |  |  | -11.5351 | -143.0356 |  |  | -0.0043085 |  | -60 | -9.02 | 1290.1814 |  | -0.0044065 |  | -60 | -9.02 | 1290.1814 |  | -0.0044822 |  | -60 | -9.02 | 1290.1814 |  | -0.0045423 |  | -60 | -9.02 | 1290.1814 |  | -0.0045912 |  | -60 | -9.02 | 1290.1814 | -0.0046319 |  | -60 | -9.02 | 1290.1814 | -0.0046661 |  | -60 | -9.02 | 1290.1814 | -0.0046954 |  | -60 | -9.02 | 1290.1814 | -0.0047207 |  | -60 | -9.02 | 1290.1814 | -0.0047428 |  | -60 | -9.02 | 1290.1814 | -0.0047623 |  | -60 | -9.02 | 1290.1814 | -0.0047796 |  | -60 | -9.02 | 1290.1814 | -0.004795 |  | -60 | -9.02 | 1290.1814 | -0.0048088 |  | -60 | -9.02 | 1290.1814 | -0.0048214 |  | -60 | -9.02 | 1290.1814 | -0.0048328 |  | -60 | -9.02 | 1290.1814 | -0.0048431 |  | -60 | -9.02 | 1290.1814 | -0.0048526 |  | -60 | -9.02 | 1290.1814 | -0.0048614 |  | -60 | -9.02 | 1290.1814 | -0.0048694 |  | -60 | -9.02 | 1290.1814 | -0.0048769 |  | -60 | -9.02 | 1290.1814
63 |  | Steel | 63 | 0.15033 |  |  | -12.1943 | -151.2091 |  |  | -0.0044789 |  | -60 | -9.02 | 1363.906 |  | -0.004555 |  | -60 | -9.02 | 1363.906 |  | -0.0046137 |  | -60 | -9.02 | 1363.906 |  | -0.0046603 |  | -60 | -9.02 | 1363.906 |  | -0.0046983 |  | -60 | -9.02 | 1363.906 | -0.0047298 |  | -60 | -9.02 | 1363.906 | -0.0047564 |  | -60 | -9.02 | 1363.906 | -0.0047791 |  | -60 | -9.02 | 1363.906 | -0.0047988 |  | -60 | -9.02 | 1363.906 | -0.0048159 |  | -60 | -9.02 | 1363.906 | -0.004831 |  | -60 | -9.02 | 1363.906 | -0.0048444 |  | -60 | -9.02 | 1363.906 | -0.0048564 |  | -60 | -9.02 | 1363.906 | -0.0048671 |  | -60 | -9.02 | 1363.906 | -0.0048769 |  | -60 | -9.02 | 1363.906 | -0.0048857 |  | -60 | -9.02 | 1363.906 | -0.0048937 |  | -60 | -9.02 | 1363.906 | -0.0049011 |  | -60 | -9.02 | 1363.906 | -0.0049079 |  | -60 | -9.02 | 1363.906 | -0.0049142 |  | -60 | -9.02 | 1363.906 | -0.0049199 |  | -60 | -9.02 | 1363.906
64 |  | Steel | 64 | 0.15033 |  |  | -12.8534 | -159.3826 |  |  | -0.0046494 |  | -60 | -9.02 | 1437.6307 |  | -0.0047034 |  | -60 | -9.02 | 1437.6307 |  | -0.0047452 |  | -60 | -9.02 | 1437.6307 |  | -0.0047784 |  | -60 | -9.02 | 1437.6307 |  | -0.0048054 |  | -60 | -9.02 | 1437.6307 | -0.0048278 |  | -60 | -9.02 | 1437.6307 | -0.0048467 |  | -60 | -9.02 | 1437.6307 | -0.0048628 |  | -60 | -9.02 | 1437.6307 | -0.0048768 |  | -60 | -9.02 | 1437.6307 | -0.004889 |  | -60 | -9.02 | 1437.6307 | -0.0048997 |  | -60 | -9.02 | 1437.6307 | -0.0049093 |  | -60 | -9.02 | 1437.6307 | -0.0049178 |  | -60 | -9.02 | 1437.6307 | -0.0049254 |  | -60 | -9.02 | 1437.6307 | -0.0049323 |  | -60 | -9.02 | 1437.6307 | -0.0049386 |  | -60 | -9.02 | 1437.6307 | -0.0049444 |  | -60 | -9.02 | 1437.6307 | -0.0049496 |  | -60 | -9.02 | 1437.6307 | -0.0049544 |  | -60 | -9.02 | 1437.6307 | -0.0049589 |  | -60 | -9.02 | 1437.6307 | -0.004963 |  | -60 | -9.02 | 1437.6307
65 |  | Steel | 65 | 0.22 |  |  | -13.3438 | -165.4628 |  |  | -0.0047761 |  | -60 | -13.2 | 2184.1092 |  | -0.0048139 |  | -60 | -13.2 | 2184.1092 |  | -0.004843 |  | -60 | -13.2 | 2184.1092 |  | -0.0048662 |  | -60 | -13.2 | 2184.1092 |  | -0.004885 |  | -60 | -13.2 | 2184.1092 | -0.0049006 |  | -60 | -13.2 | 2184.1092 | -0.0049138 |  | -60 | -13.2 | 2184.1092 | -0.0049251 |  | -60 | -13.2 | 2184.1092 | -0.0049349 |  | -60 | -13.2 | 2184.1092 | -0.0049434 |  | -60 | -13.2 | 2184.1092 | -0.0049509 |  | -60 | -13.2 | 2184.1092 | -0.0049575 |  | -60 | -13.2 | 2184.1092 | -0.0049635 |  | -60 | -13.2 | 2184.1092 | -0.0049688 |  | -60 | -13.2 | 2184.1092 | -0.0049736 |  | -60 | -13.2 | 2184.1092 | -0.004978 |  | -60 | -13.2 | 2184.1092 | -0.004982 |  | -60 | -13.2 | 2184.1092 | -0.0049857 |  | -60 | -13.2 | 2184.1092 | -0.004989 |  | -60 | -13.2 | 2184.1092 | -0.0049921 |  | -60 | -13.2 | 2184.1092 | -0.004995 |  | -60 | -13.2 | 2184.1092
66 |  | Steel | 66 | 0.22 |  |  | -13.6653 | -169.4499 |  |  | -0.0048593 |  | -60 | -13.2 | 2236.7383 |  | -0.0048863 |  | -60 | -13.2 | 2236.7383 |  | -0.0049071 |  | -60 | -13.2 | 2236.7383 |  | -0.0049237 |  | -60 | -13.2 | 2236.7383 |  | -0.0049372 |  | -60 | -13.2 | 2236.7383 | -0.0049484 |  | -60 | -13.2 | 2236.7383 | -0.0049579 |  | -60 | -13.2 | 2236.7383 | -0.004966 |  | -60 | -13.2 | 2236.7383 | -0.0049729 |  | -60 | -13.2 | 2236.7383 | -0.004979 |  | -60 | -13.2 | 2236.7383 | -0.0049844 |  | -60 | -13.2 | 2236.7383 | -0.0049892 |  | -60 | -13.2 | 2236.7383 | -0.0049934 |  | -60 | -13.2 | 2236.7383 | -0.0049972 |  | -60 | -13.2 | 2236.7383 | -0.0050007 |  | -60 | -13.2 | 2236.7383 | -0.0050038 |  | -60 | -13.2 | 2236.7383 | -0.0050067 |  | -60 | -13.2 | 2236.7383 | -0.0050093 |  | -60 | -13.2 | 2236.7383 | -0.0050117 |  | -60 | -13.2 | 2236.7383 | -0.0050139 |  | -60 | -13.2 | 2236.7383 | -0.005016 |  | -60 | -13.2 | 2236.7383
67 |  | Steel | 67 | 0.22 |  |  | -13.9868 | -173.4369 |  |  | -0.0049424 |  | -60 | -13.2 | 2289.3675 |  | -0.0049587 |  | -60 | -13.2 | 2289.3675 |  | -0.0049713 |  | -60 | -13.2 | 2289.3675 |  | -0.0049813 |  | -60 | -13.2 | 2289.3675 |  | -0.0049895 |  | -60 | -13.2 | 2289.3675 | -0.0049962 |  | -60 | -13.2 | 2289.3675 | -0.0050019 |  | -60 | -13.2 | 2289.3675 | -0.0050068 |  | -60 | -13.2 | 2289.3675 | -0.005011 |  | -60 | -13.2 | 2289.3675 | -0.0050147 |  | -60 | -13.2 | 2289.3675 | -0.0050179 |  | -60 | -13.2 | 2289.3675 | -0.0050208 |  | -60 | -13.2 | 2289.3675 | -0.0050234 |  | -60 | -13.2 | 2289.3675 | -0.0050257 |  | -60 | -13.2 | 2289.3675 | -0.0050278 |  | -60 | -13.2 | 2289.3675 | -0.0050296 |  | -60 | -13.2 | 2289.3675 | -0.0050314 |  | -60 | -13.2 | 2289.3675 | -0.005033 |  | -60 | -13.2 | 2289.3675 | -0.0050344 |  | -60 | -13.2 | 2289.3675 | -0.0050358 |  | -60 | -13.2 | 2289.3675 | -0.005037 |  | -60 | -13.2 | 2289.3675
68 |  | Steel | 68 | 0.22 |  |  | -14.3084 | -177.424 |  |  | -0.0050255 |  | -60 | -13.2 | 2341.9966 |  | -0.0050311 |  | -60 | -13.2 | 2341.9966 |  | -0.0050354 |  | -60 | -13.2 | 2341.9966 |  | -0.0050389 |  | -60 | -13.2 | 2341.9966 |  | -0.0050417 |  | -60 | -13.2 | 2341.9966 | -0.005044 |  | -60 | -13.2 | 2341.9966 | -0.005046 |  | -60 | -13.2 | 2341.9966 | -0.0050476 |  | -60 | -13.2 | 2341.9966 | -0.0050491 |  | -60 | -13.2 | 2341.9966 | -0.0050503 |  | -60 | -13.2 | 2341.9966 | -0.0050514 |  | -60 | -13.2 | 2341.9966 | -0.0050524 |  | -60 | -13.2 | 2341.9966 | -0.0050533 |  | -60 | -13.2 | 2341.9966 | -0.0050541 |  | -60 | -13.2 | 2341.9966 | -0.0050548 |  | -60 | -13.2 | 2341.9966 | -0.0050555 |  | -60 | -13.2 | 2341.9966 | -0.0050561 |  | -60 | -13.2 | 2341.9966 | -0.0050566 |  | -60 | -13.2 | 2341.9966 | -0.0050571 |  | -60 | -13.2 | 2341.9966 | -0.0050576 |  | -60 | -13.2 | 2341.9966 | -0.005058 |  | -60 | -13.2 | 2341.9966
69 |  | Steel | 69 | 0.0465 |  |  | -52.224 | -172.3598 |  |  | -0.0049199 |  | -60 | -2.79 | 480.8838 |  | -0.0049391 |  | -60 | -2.79 | 480.8838 |  | -0.004954 |  | -60 | -2.79 | 480.8838 |  | -0.0049657 |  | -60 | -2.79 | 480.8838 |  | -0.0049753 |  | -60 | -2.79 | 480.8838 | -0.0049833 |  | -60 | -2.79 | 480.8838 | -0.00499 |  | -60 | -2.79 | 480.8838 | -0.0049958 |  | -60 | -2.79 | 480.8838 | -0.0050007 |  | -60 | -2.79 | 480.8838 | -0.005005 |  | -60 | -2.79 | 480.8838 | -0.0050089 |  | -60 | -2.79 | 480.8838 | -0.0050122 |  | -60 | -2.79 | 480.8838 | -0.0050153 |  | -60 | -2.79 | 480.8838 | -0.005018 |  | -60 | -2.79 | 480.8838 | -0.0050204 |  | -60 | -2.79 | 480.8838 | -0.0050227 |  | -60 | -2.79 | 480.8838 | -0.0050247 |  | -60 | -2.79 | 480.8838 | -0.0050266 |  | -60 | -2.79 | 480.8838 | -0.0050283 |  | -60 | -2.79 | 480.8838 | -0.0050299 |  | -60 | -2.79 | 480.8838 | -0.0050313 |  | -60 | -2.79 | 480.8838
70 |  | Steel | 70 | 0.0465 |  |  | -48.6357 | -172.6492 |  |  | -0.004926 |  | -60 | -2.79 | 481.6912 |  | -0.0049444 |  | -60 | -2.79 | 481.6912 |  | -0.0049586 |  | -60 | -2.79 | 481.6912 |  | -0.0049699 |  | -60 | -2.79 | 481.6912 |  | -0.0049791 |  | -60 | -2.79 | 481.6912 | -0.0049868 |  | -60 | -2.79 | 481.6912 | -0.0049932 |  | -60 | -2.79 | 481.6912 | -0.0049987 |  | -60 | -2.79 | 481.6912 | -0.0050035 |  | -60 | -2.79 | 481.6912 | -0.0050076 |  | -60 | -2.79 | 481.6912 | -0.0050113 |  | -60 | -2.79 | 481.6912 | -0.0050145 |  | -60 | -2.79 | 481.6912 | -0.0050174 |  | -60 | -2.79 | 481.6912 | -0.0050201 |  | -60 | -2.79 | 481.6912 | -0.0050224 |  | -60 | -2.79 | 481.6912 | -0.0050245 |  | -60 | -2.79 | 481.6912 | -0.0050265 |  | -60 | -2.79 | 481.6912 | -0.0050283 |  | -60 | -2.79 | 481.6912 | -0.0050299 |  | -60 | -2.79 | 481.6912 | -0.0050314 |  | -60 | -2.79 | 481.6912 | -0.0050328 |  | -60 | -2.79 | 481.6912
71 |  | Steel | 71 | 0.0465 |  |  | -45.0473 | -172.9385 |  |  | -0.004932 |  | -60 | -2.79 | 482.4985 |  | -0.0049497 |  | -60 | -2.79 | 482.4985 |  | -0.0049633 |  | -60 | -2.79 | 482.4985 |  | -0.0049741 |  | -60 | -2.79 | 482.4985 |  | -0.0049829 |  | -60 | -2.79 | 482.4985 | -0.0049902 |  | -60 | -2.79 | 482.4985 | -0.0049964 |  | -60 | -2.79 | 482.4985 | -0.0050017 |  | -60 | -2.79 | 482.4985 | -0.0050062 |  | -60 | -2.79 | 482.4985 | -0.0050102 |  | -60 | -2.79 | 482.4985 | -0.0050137 |  | -60 | -2.79 | 482.4985 | -0.0050168 |  | -60 | -2.79 | 482.4985 | -0.0050196 |  | -60 | -2.79 | 482.4985 | -0.0050221 |  | -60 | -2.79 | 482.4985 | -0.0050244 |  | -60 | -2.79 | 482.4985 | -0.0050264 |  | -60 | -2.79 | 482.4985 | -0.0050283 |  | -60 | -2.79 | 482.4985 | -0.00503 |  | -60 | -2.79 | 482.4985 | -0.0050316 |  | -60 | -2.79 | 482.4985 | -0.005033 |  | -60 | -2.79 | 482.4985 | -0.0050344 |  | -60 | -2.79 | 482.4985
72 |  | Steel | 72 | 0.0465 |  |  | -41.4589 | -173.2279 |  |  | -0.004938 |  | -60 | -2.79 | 483.3059 |  | -0.0049549 |  | -60 | -2.79 | 483.3059 |  | -0.0049679 |  | -60 | -2.79 | 483.3059 |  | -0.0049783 |  | -60 | -2.79 | 483.3059 |  | -0.0049867 |  | -60 | -2.79 | 483.3059 | -0.0049937 |  | -60 | -2.79 | 483.3059 | -0.0049996 |  | -60 | -2.79 | 483.3059 | -0.0050046 |  | -60 | -2.79 | 483.3059 | -0.005009 |  | -60 | -2.79 | 483.3059 | -0.0050128 |  | -60 | -2.79 | 483.3059 | -0.0050162 |  | -60 | -2.79 | 483.3059 | -0.0050191 |  | -60 | -2.79 | 483.3059 | -0.0050218 |  | -60 | -2.79 | 483.3059 | -0.0050242 |  | -60 | -2.79 | 483.3059 | -0.0050263 |  | -60 | -2.79 | 483.3059 | -0.0050283 |  | -60 | -2.79 | 483.3059 | -0.0050301 |  | -60 | -2.79 | 483.3059 | -0.0050317 |  | -60 | -2.79 | 483.3059 | -0.0050332 |  | -60 | -2.79 | 483.3059 | -0.0050346 |  | -60 | -2.79 | 483.3059 | -0.0050359 |  | -60 | -2.79 | 483.3059
73 |  | Steel | 73 | 0.0465 |  |  | -37.8706 | -173.5173 |  |  | -0.0049441 |  | -60 | -2.79 | 484.1133 |  | -0.0049602 |  | -60 | -2.79 | 484.1133 |  | -0.0049726 |  | -60 | -2.79 | 484.1133 |  | -0.0049825 |  | -60 | -2.79 | 484.1133 |  | -0.0049905 |  | -60 | -2.79 | 484.1133 | -0.0049972 |  | -60 | -2.79 | 484.1133 | -0.0050028 |  | -60 | -2.79 | 484.1133 | -0.0050076 |  | -60 | -2.79 | 484.1133 | -0.0050118 |  | -60 | -2.79 | 484.1133 | -0.0050154 |  | -60 | -2.79 | 484.1133 | -0.0050186 |  | -60 | -2.79 | 484.1133 | -0.0050214 |  | -60 | -2.79 | 484.1133 | -0.005024 |  | -60 | -2.79 | 484.1133 | -0.0050262 |  | -60 | -2.79 | 484.1133 | -0.0050283 |  | -60 | -2.79 | 484.1133 | -0.0050302 |  | -60 | -2.79 | 484.1133 | -0.0050319 |  | -60 | -2.79 | 484.1133 | -0.0050334 |  | -60 | -2.79 | 484.1133 | -0.0050349 |  | -60 | -2.79 | 484.1133 | -0.0050362 |  | -60 | -2.79 | 484.1133 | -0.0050374 |  | -60 | -2.79 | 484.1133
74 |  | Steel | 74 | 0.0465 |  |  | -34.2822 | -173.8067 |  |  | -0.0049501 |  | -60 | -2.79 | 484.9207 |  | -0.0049654 |  | -60 | -2.79 | 484.9207 |  | -0.0049772 |  | -60 | -2.79 | 484.9207 |  | -0.0049866 |  | -60 | -2.79 | 484.9207 |  | -0.0049943 |  | -60 | -2.79 | 484.9207 | -0.0050006 |  | -60 | -2.79 | 484.9207 | -0.005006 |  | -60 | -2.79 | 484.9207 | -0.0050106 |  | -60 | -2.79 | 484.9207 | -0.0050145 |  | -60 | -2.79 | 484.9207 | -0.005018 |  | -60 | -2.79 | 484.9207 | -0.005021 |  | -60 | -2.79 | 484.9207 | -0.0050237 |  | -60 | -2.79 | 484.9207 | -0.0050261 |  | -60 | -2.79 | 484.9207 | -0.0050283 |  | -60 | -2.79 | 484.9207 | -0.0050303 |  | -60 | -2.79 | 484.9207 | -0.005032 |  | -60 | -2.79 | 484.9207 | -0.0050337 |  | -60 | -2.79 | 484.9207 | -0.0050352 |  | -60 | -2.79 | 484.9207 | -0.0050365 |  | -60 | -2.79 | 484.9207 | -0.0050378 |  | -60 | -2.79 | 484.9207 | -0.0050389 |  | -60 | -2.79 | 484.9207
75 |  | Steel | 75 | 0.0465 |  |  | -30.6939 | -174.0961 |  |  | -0.0049561 |  | -60 | -2.79 | 485.7281 |  | -0.0049707 |  | -60 | -2.79 | 485.7281 |  | -0.0049819 |  | -60 | -2.79 | 485.7281 |  | -0.0049908 |  | -60 | -2.79 | 485.7281 |  | -0.0049981 |  | -60 | -2.79 | 485.7281 | -0.0050041 |  | -60 | -2.79 | 485.7281 | -0.0050092 |  | -60 | -2.79 | 485.7281 | -0.0050135 |  | -60 | -2.79 | 485.7281 | -0.0050173 |  | -60 | -2.79 | 485.7281 | -0.0050206 |  | -60 | -2.79 | 485.7281 | -0.0050235 |  | -60 | -2.79 | 485.7281 | -0.005026 |  | -60 | -2.79 | 485.7281 | -0.0050283 |  | -60 | -2.79 | 485.7281 | -0.0050304 |  | -60 | -2.79 | 485.7281 | -0.0050322 |  | -60 | -2.79 | 485.7281 | -0.0050339 |  | -60 | -2.79 | 485.7281 | -0.0050355 |  | -60 | -2.79 | 485.7281 | -0.0050369 |  | -60 | -2.79 | 485.7281 | -0.0050382 |  | -60 | -2.79 | 485.7281 | -0.0050394 |  | -60 | -2.79 | 485.7281 | -0.0050405 |  | -60 | -2.79 | 485.7281
76 |  | Steel | 76 | 0.0465 |  |  | -27.1055 | -174.3855 |  |  | -0.0049622 |  | -60 | -2.79 | 486.5354 |  | -0.0049759 |  | -60 | -2.79 | 486.5354 |  | -0.0049866 |  | -60 | -2.79 | 486.5354 |  | -0.004995 |  | -60 | -2.79 | 486.5354 |  | -0.0050019 |  | -60 | -2.79 | 486.5354 | -0.0050076 |  | -60 | -2.79 | 486.5354 | -0.0050124 |  | -60 | -2.79 | 486.5354 | -0.0050165 |  | -60 | -2.79 | 486.5354 | -0.0050201 |  | -60 | -2.79 | 486.5354 | -0.0050232 |  | -60 | -2.79 | 486.5354 | -0.0050259 |  | -60 | -2.79 | 486.5354 | -0.0050283 |  | -60 | -2.79 | 486.5354 | -0.0050305 |  | -60 | -2.79 | 486.5354 | -0.0050324 |  | -60 | -2.79 | 486.5354 | -0.0050342 |  | -60 | -2.79 | 486.5354 | -0.0050358 |  | -60 | -2.79 | 486.5354 | -0.0050373 |  | -60 | -2.79 | 486.5354 | -0.0050386 |  | -60 | -2.79 | 486.5354 | -0.0050398 |  | -60 | -2.79 | 486.5354 | -0.0050409 |  | -60 | -2.79 | 486.5354 | -0.005042 |  | -60 | -2.79 | 486.5354
77 |  | Steel | 77 | 0.0465 |  |  | -23.5172 | -174.6748 |  |  | -0.0049682 |  | -60 | -2.79 | 487.3428 |  | -0.0049812 |  | -60 | -2.79 | 487.3428 |  | -0.0049912 |  | -60 | -2.79 | 487.3428 |  | -0.0049992 |  | -60 | -2.79 | 487.3428 |  | -0.0050057 |  | -60 | -2.79 | 487.3428 | -0.005011 |  | -60 | -2.79 | 487.3428 | -0.0050156 |  | -60 | -2.79 | 487.3428 | -0.0050195 |  | -60 | -2.79 | 487.3428 | -0.0050228 |  | -60 | -2.79 | 487.3428 | -0.0050258 |  | -60 | -2.79 | 487.3428 | -0.0050283 |  | -60 | -2.79 | 487.3428 | -0.0050306 |  | -60 | -2.79 | 487.3428 | -0.0050327 |  | -60 | -2.79 | 487.3428 | -0.0050345 |  | -60 | -2.79 | 487.3428 | -0.0050362 |  | -60 | -2.79 | 487.3428 | -0.0050377 |  | -60 | -2.79 | 487.3428 | -0.005039 |  | -60 | -2.79 | 487.3428 | -0.0050403 |  | -60 | -2.79 | 487.3428 | -0.0050415 |  | -60 | -2.79 | 487.3428 | -0.0050425 |  | -60 | -2.79 | 487.3428 | -0.0050435 |  | -60 | -2.79 | 487.3428
78 |  | Steel | 78 | 0.0465 |  |  | -19.9288 | -174.9642 |  |  | -0.0049742 |  | -60 | -2.79 | 488.1502 |  | -0.0049864 |  | -60 | -2.79 | 488.1502 |  | -0.0049959 |  | -60 | -2.79 | 488.1502 |  | -0.0050034 |  | -60 | -2.79 | 488.1502 |  | -0.0050095 |  | -60 | -2.79 | 488.1502 | -0.0050145 |  | -60 | -2.79 | 488.1502 | -0.0050188 |  | -60 | -2.79 | 488.1502 | -0.0050224 |  | -60 | -2.79 | 488.1502 | -0.0050256 |  | -60 | -2.79 | 488.1502 | -0.0050283 |  | -60 | -2.79 | 488.1502 | -0.0050308 |  | -60 | -2.79 | 488.1502 | -0.0050329 |  | -60 | -2.79 | 488.1502 | -0.0050348 |  | -60 | -2.79 | 488.1502 | -0.0050366 |  | -60 | -2.79 | 488.1502 | -0.0050381 |  | -60 | -2.79 | 488.1502 | -0.0050395 |  | -60 | -2.79 | 488.1502 | -0.0050408 |  | -60 | -2.79 | 488.1502 | -0.005042 |  | -60 | -2.79 | 488.1502 | -0.0050431 |  | -60 | -2.79 | 488.1502 | -0.0050441 |  | -60 | -2.79 | 488.1502 | -0.005045 |  | -60 | -2.79 | 488.1502
79 |  | Steel | 79 | 0.0465 |  |  | 35.2919 | -179.4175 |  |  | -0.0050671 |  | -60 | -2.79 | 500.5749 |  | -0.0050673 |  | -60 | -2.79 | 500.5749 |  | -0.0050675 |  | -60 | -2.79 | 500.5749 |  | -0.0050677 |  | -60 | -2.79 | 500.5749 |  | -0.0050678 |  | -60 | -2.79 | 500.5749 | -0.0050679 |  | -60 | -2.79 | 500.5749 | -0.005068 |  | -60 | -2.79 | 500.5749 | -0.005068 |  | -60 | -2.79 | 500.5749 | -0.0050681 |  | -60 | -2.79 | 500.5749 | -0.0050682 |  | -60 | -2.79 | 500.5749 | -0.0050682 |  | -60 | -2.79 | 500.5749 | -0.0050683 |  | -60 | -2.79 | 500.5749 | -0.0050683 |  | -60 | -2.79 | 500.5749 | -0.0050683 |  | -60 | -2.79 | 500.5749 | -0.0050684 |  | -60 | -2.79 | 500.5749 | -0.0050684 |  | -60 | -2.79 | 500.5749 | -0.0050684 |  | -60 | -2.79 | 500.5749 | -0.0050684 |  | -60 | -2.79 | 500.5749 | -0.0050685 |  | -60 | -2.79 | 500.5749 | -0.0050685 |  | -60 | -2.79 | 500.5749 | -0.0050685 |  | -60 | -2.79 | 500.5749
80 |  | Steel | 80 | 0.0465 |  |  | 30.5074 | -179.0317 |  |  | -0.005059 |  | -60 | -2.79 | 499.4984 |  | -0.0050603 |  | -60 | -2.79 | 499.4984 |  | -0.0050613 |  | -60 | -2.79 | 499.4984 |  | -0.0050621 |  | -60 | -2.79 | 499.4984 |  | -0.0050627 |  | -60 | -2.79 | 499.4984 | -0.0050633 |  | -60 | -2.79 | 499.4984 | -0.0050637 |  | -60 | -2.79 | 499.4984 | -0.0050641 |  | -60 | -2.79 | 499.4984 | -0.0050644 |  | -60 | -2.79 | 499.4984 | -0.0050647 |  | -60 | -2.79 | 499.4984 | -0.005065 |  | -60 | -2.79 | 499.4984 | -0.0050652 |  | -60 | -2.79 | 499.4984 | -0.0050654 |  | -60 | -2.79 | 499.4984 | -0.0050656 |  | -60 | -2.79 | 499.4984 | -0.0050657 |  | -60 | -2.79 | 499.4984 | -0.0050659 |  | -60 | -2.79 | 499.4984 | -0.005066 |  | -60 | -2.79 | 499.4984 | -0.0050661 |  | -60 | -2.79 | 499.4984 | -0.0050663 |  | -60 | -2.79 | 499.4984 | -0.0050664 |  | -60 | -2.79 | 499.4984 | -0.0050665 |  | -60 | -2.79 | 499.4984
81 |  | Steel | 81 | 0.0465 |  |  | 25.7229 | -178.6458 |  |  | -0.005051 |  | -60 | -2.79 | 498.4218 |  | -0.0050533 |  | -60 | -2.79 | 498.4218 |  | -0.0050551 |  | -60 | -2.79 | 498.4218 |  | -0.0050565 |  | -60 | -2.79 | 498.4218 |  | -0.0050577 |  | -60 | -2.79 | 498.4218 | -0.0050586 |  | -60 | -2.79 | 498.4218 | -0.0050594 |  | -60 | -2.79 | 498.4218 | -0.0050601 |  | -60 | -2.79 | 498.4218 | -0.0050607 |  | -60 | -2.79 | 498.4218 | -0.0050613 |  | -60 | -2.79 | 498.4218 | -0.0050617 |  | -60 | -2.79 | 498.4218 | -0.0050621 |  | -60 | -2.79 | 498.4218 | -0.0050625 |  | -60 | -2.79 | 498.4218 | -0.0050628 |  | -60 | -2.79 | 498.4218 | -0.0050631 |  | -60 | -2.79 | 498.4218 | -0.0050634 |  | -60 | -2.79 | 498.4218 | -0.0050636 |  | -60 | -2.79 | 498.4218 | -0.0050639 |  | -60 | -2.79 | 498.4218 | -0.0050641 |  | -60 | -2.79 | 498.4218 | -0.0050643 |  | -60 | -2.79 | 498.4218 | -0.0050644 |  | -60 | -2.79 | 498.4218
82 |  | Steel | 82 | 0.0465 |  |  | 20.9385 | -178.26 |  |  | -0.005043 |  | -60 | -2.79 | 497.3453 |  | -0.0050463 |  | -60 | -2.79 | 497.3453 |  | -0.0050489 |  | -60 | -2.79 | 497.3453 |  | -0.005051 |  | -60 | -2.79 | 497.3453 |  | -0.0050526 |  | -60 | -2.79 | 497.3453 | -0.005054 |  | -60 | -2.79 | 497.3453 | -0.0050552 |  | -60 | -2.79 | 497.3453 | -0.0050562 |  | -60 | -2.79 | 497.3453 | -0.0050571 |  | -60 | -2.79 | 497.3453 | -0.0050578 |  | -60 | -2.79 | 497.3453 | -0.0050585 |  | -60 | -2.79 | 497.3453 | -0.0050591 |  | -60 | -2.79 | 497.3453 | -0.0050596 |  | -60 | -2.79 | 497.3453 | -0.0050601 |  | -60 | -2.79 | 497.3453 | -0.0050605 |  | -60 | -2.79 | 497.3453 | -0.0050609 |  | -60 | -2.79 | 497.3453 | -0.0050612 |  | -60 | -2.79 | 497.3453 | -0.0050616 |  | -60 | -2.79 | 497.3453 | -0.0050619 |  | -60 | -2.79 | 497.3453 | -0.0050621 |  | -60 | -2.79 | 497.3453 | -0.0050624 |  | -60 | -2.79 | 497.3453
83 |  | Steel | 83 | 0.0465 |  |  | 16.154 | -177.8741 |  |  | -0.0050349 |  | -60 | -2.79 | 496.2688 |  | -0.0050393 |  | -60 | -2.79 | 496.2688 |  | -0.0050427 |  | -60 | -2.79 | 496.2688 |  | -0.0050454 |  | -60 | -2.79 | 496.2688 |  | -0.0050476 |  | -60 | -2.79 | 496.2688 | -0.0050494 |  | -60 | -2.79 | 496.2688 | -0.0050509 |  | -60 | -2.79 | 496.2688 | -0.0050522 |  | -60 | -2.79 | 496.2688 | -0.0050534 |  | -60 | -2.79 | 496.2688 | -0.0050544 |  | -60 | -2.79 | 496.2688 | -0.0050552 |  | -60 | -2.79 | 496.2688 | -0.005056 |  | -60 | -2.79 | 496.2688 | -0.0050567 |  | -60 | -2.79 | 496.2688 | -0.0050573 |  | -60 | -2.79 | 496.2688 | -0.0050579 |  | -60 | -2.79 | 496.2688 | -0.0050584 |  | -60 | -2.79 | 496.2688 | -0.0050589 |  | -60 | -2.79 | 496.2688 | -0.0050593 |  | -60 | -2.79 | 496.2688 | -0.0050597 |  | -60 | -2.79 | 496.2688 | -0.00506 |  | -60 | -2.79 | 496.2688 | -0.0050604 |  | -60 | -2.79 | 496.2688
84 |  | Steel | 84 | 0.0465 |  |  | 11.3695 | -177.4883 |  |  | -0.0050269 |  | -60 | -2.79 | 495.1923 |  | -0.0050323 |  | -60 | -2.79 | 495.1923 |  | -0.0050365 |  | -60 | -2.79 | 495.1923 |  | -0.0050398 |  | -60 | -2.79 | 495.1923 |  | -0.0050425 |  | -60 | -2.79 | 495.1923 | -0.0050448 |  | -60 | -2.79 | 495.1923 | -0.0050467 |  | -60 | -2.79 | 495.1923 | -0.0050483 |  | -60 | -2.79 | 495.1923 | -0.0050497 |  | -60 | -2.79 | 495.1923 | -0.0050509 |  | -60 | -2.79 | 495.1923 | -0.005052 |  | -60 | -2.79 | 495.1923 | -0.0050529 |  | -60 | -2.79 | 495.1923 | -0.0050538 |  | -60 | -2.79 | 495.1923 | -0.0050546 |  | -60 | -2.79 | 495.1923 | -0.0050553 |  | -60 | -2.79 | 495.1923 | -0.0050559 |  | -60 | -2.79 | 495.1923 | -0.0050565 |  | -60 | -2.79 | 495.1923 | -0.005057 |  | -60 | -2.79 | 495.1923 | -0.0050575 |  | -60 | -2.79 | 495.1923 | -0.0050579 |  | -60 | -2.79 | 495.1923 | -0.0050583 |  | -60 | -2.79 | 495.1923
85 |  | Steel | 85 | 0.0465 |  |  | 6.5851 | -177.1024 |  |  | -0.0050188 |  | -60 | -2.79 | 494.1158 |  | -0.0050253 |  | -60 | -2.79 | 494.1158 |  | -0.0050303 |  | -60 | -2.79 | 494.1158 |  | -0.0050342 |  | -60 | -2.79 | 494.1158 |  | -0.0050375 |  | -60 | -2.79 | 494.1158 | -0.0050401 |  | -60 | -2.79 | 494.1158 | -0.0050424 |  | -60 | -2.79 | 494.1158 | -0.0050443 |  | -60 | -2.79 | 494.1158 | -0.005046 |  | -60 | -2.79 | 494.1158 | -0.0050475 |  | -60 | -2.79 | 494.1158 | -0.0050487 |  | -60 | -2.79 | 494.1158 | -0.0050499 |  | -60 | -2.79 | 494.1158 | -0.0050509 |  | -60 | -2.79 | 494.1158 | -0.0050518 |  | -60 | -2.79 | 494.1158 | -0.0050526 |  | -60 | -2.79 | 494.1158 | -0.0050534 |  | -60 | -2.79 | 494.1158 | -0.0050541 |  | -60 | -2.79 | 494.1158 | -0.0050547 |  | -60 | -2.79 | 494.1158 | -0.0050553 |  | -60 | -2.79 | 494.1158 | -0.0050558 |  | -60 | -2.79 | 494.1158 | -0.0050563 |  | -60 | -2.79 | 494.1158
86 |  | Steel | 86 | 0.0465 |  |  | 1.8006 | -176.7166 |  |  | -0.0050108 |  | -60 | -2.79 | 493.0393 |  | -0.0050183 |  | -60 | -2.79 | 493.0393 |  | -0.0050241 |  | -60 | -2.79 | 493.0393 |  | -0.0050287 |  | -60 | -2.79 | 493.0393 |  | -0.0050324 |  | -60 | -2.79 | 493.0393 | -0.0050355 |  | -60 | -2.79 | 493.0393 | -0.0050381 |  | -60 | -2.79 | 493.0393 | -0.0050404 |  | -60 | -2.79 | 493.0393 | -0.0050423 |  | -60 | -2.79 | 493.0393 | -0.005044 |  | -60 | -2.79 | 493.0393 | -0.0050455 |  | -60 | -2.79 | 493.0393 | -0.0050468 |  | -60 | -2.79 | 493.0393 | -0.005048 |  | -60 | -2.79 | 493.0393 | -0.0050491 |  | -60 | -2.79 | 493.0393 | -0.00505 |  | -60 | -2.79 | 493.0393 | -0.0050509 |  | -60 | -2.79 | 493.0393 | -0.0050517 |  | -60 | -2.79 | 493.0393 | -0.0050524 |  | -60 | -2.79 | 493.0393 | -0.0050531 |  | -60 | -2.79 | 493.0393 | -0.0050537 |  | -60 | -2.79 | 493.0393 | -0.0050543 |  | -60 | -2.79 | 493.0393
87 |  | Steel | 87 | 0.0465 |  |  | -2.9839 | -176.3308 |  |  | -0.0050027 |  | -60 | -2.79 | 491.9628 |  | -0.0050113 |  | -60 | -2.79 | 491.9628 |  | -0.0050179 |  | -60 | -2.79 | 491.9628 |  | -0.0050231 |  | -60 | -2.79 | 491.9628 |  | -0.0050274 |  | -60 | -2.79 | 491.9628 | -0.0050309 |  | -60 | -2.79 | 491.9628 | -0.0050339 |  | -60 | -2.79 | 491.9628 | -0.0050364 |  | -60 | -2.79 | 491.9628 | -0.0050386 |  | -60 | -2.79 | 491.9628 | -0.0050406 |  | -60 | -2.79 | 491.9628 | -0.0050423 |  | -60 | -2.79 | 491.9628 | -0.0050438 |  | -60 | -2.79 | 491.9628 | -0.0050451 |  | -60 | -2.79 | 491.9628 | -0.0050463 |  | -60 | -2.79 | 491.9628 | -0.0050474 |  | -60 | -2.79 | 491.9628 | -0.0050484 |  | -60 | -2.79 | 491.9628 | -0.0050493 |  | -60 | -2.79 | 491.9628 | -0.0050501 |  | -60 | -2.79 | 491.9628 | -0.0050509 |  | -60 | -2.79 | 491.9628 | -0.0050516 |  | -60 | -2.79 | 491.9628 | -0.0050522 |  | -60 | -2.79 | 491.9628
88 |  | Steel | 88 | 0.0465 |  |  | -7.7683 | -175.9449 |  |  | -0.0049947 |  | -60 | -2.79 | 490.8863 |  | -0.0050043 |  | -60 | -2.79 | 490.8863 |  | -0.0050116 |  | -60 | -2.79 | 490.8863 |  | -0.0050175 |  | -60 | -2.79 | 490.8863 |  | -0.0050223 |  | -60 | -2.79 | 490.8863 | -0.0050263 |  | -60 | -2.79 | 490.8863 | -0.0050296 |  | -60 | -2.79 | 490.8863 | -0.0050325 |  | -60 | -2.79 | 490.8863 | -0.0050349 |  | -60 | -2.79 | 490.8863 | -0.0050371 |  | -60 | -2.79 | 490.8863 | -0.005039 |  | -60 | -2.79 | 490.8863 | -0.0050407 |  | -60 | -2.79 | 490.8863 | -0.0050422 |  | -60 | -2.79 | 490.8863 | -0.0050436 |  | -60 | -2.79 | 490.8863 | -0.0050448 |  | -60 | -2.79 | 490.8863 | -0.0050459 |  | -60 | -2.79 | 490.8863 | -0.0050469 |  | -60 | -2.79 | 490.8863 | -0.0050478 |  | -60 | -2.79 | 490.8863 | -0.0050487 |  | -60 | -2.79 | 490.8863 | -0.0050495 |  | -60 | -2.79 | 490.8863 | -0.0050502 |  | -60 | -2.79 | 490.8863
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33 |  | Concrete | 1 | 55.8 |  |  | -35.4526 | 177.424 |  |  | 0.0023732 | 2.0273 |  | 113.1226 | 20070.6712 |  | 0.001414 | 2.5039 |  | 139.7184 | 24789.3955 |  | 0.00067377 | 1.6697 |  | 93.1707 | 16530.7228 |  | 8.5296e-05 | 0.25934 |  | 14.4714 | 2567.5661 |  | -0.00039379 | 0 |  | 0 | 0 | -0.00079138 | 0 |  | 0 | 0 | -0.0011267 | 0 |  | 0 | 0 | -0.0014132 | 0 |  | 0 | 0 | -0.0016609 | 0 |  | 0 | 0 | -0.0018772 | 0 |  | 0 | 0 | -0.0020676 | 0 |  | 0 | 0 | -0.0022366 | 0 |  | 0 | 0 | -0.0023876 | 0 |  | 0 | 0 | -0.0025233 | 0 |  | 0 | 0 | -0.0026459 | 0 |  | 0 | 0 | -0.0027573 | 0 |  | 0 | 0 | -0.0028589 | 0 |  | 0 | 0 | -0.0029519 | 0 |  | 0 | 0 | -0.0030374 | 0 |  | 0 | 0 | -0.0031163 | 0 |  | 0 | 0 | -0.0031893 | 0 |  | 0 | 0
34 |  | Concrete | 2 | 55.8 |  |  | -30.6682 | 177.0381 |  |  | 0.0023651 | 2.0386 |  | 113.7537 | 20138.7492 |  | 0.0014069 | 2.5009 |  | 139.5517 | 24705.9655 |  | 0.00066757 | 1.6583 |  | 92.5333 | 16381.9177 |  | 7.9724e-05 | 0.24283 |  | 13.5497 | 2398.8198 |  | -0.00039884 | 0 |  | 0 | 0 | -0.00079601 | 0 |  | 0 | 0 | -0.0011309 | 0 |  | 0 | 0 | -0.0014171 | 0 |  | 0 | 0 | -0.0016646 | 0 |  | 0 | 0 | -0.0018806 | 0 |  | 0 | 0 | -0.0020709 | 0 |  | 0 | 0 | -0.0022397 | 0 |  | 0 | 0 | -0.0023905 | 0 |  | 0 | 0 | -0.0025261 | 0 |  | 0 | 0 | -0.0026486 | 0 |  | 0 | 0 | -0.0027598 | 0 |  | 0 | 0 | -0.0028613 | 0 |  | 0 | 0 | -0.0029542 | 0 |  | 0 | 0 | -0.0030396 | 0 |  | 0 | 0 | -0.0031184 | 0 |  | 0 | 0 | -0.0031913 | 0 |  | 0 | 0
35 |  | Concrete | 3 | 55.8 |  |  | -25.8837 | 176.6523 |  |  | 0.0023571 | 2.0498 |  | 114.3779 | 20205.121 |  | 0.0013999 | 2.4978 |  | 139.3797 | 24621.739 |  | 0.00066136 | 1.6468 |  | 91.8917 | 16232.8785 |  | 7.4152e-05 | 0.22625 |  | 12.6248 | 2230.1999 |  | -0.00040389 | 0 |  | 0 | 0 | -0.00080063 | 0 |  | 0 | 0 | -0.0011352 | 0 |  | 0 | 0 | -0.0014211 | 0 |  | 0 | 0 | -0.0016683 | 0 |  | 0 | 0 | -0.0018841 | 0 |  | 0 | 0 | -0.0020741 | 0 |  | 0 | 0 | -0.0022427 | 0 |  | 0 | 0 | -0.0023934 | 0 |  | 0 | 0 | -0.0025288 | 0 |  | 0 | 0 | -0.0026512 | 0 |  | 0 | 0 | -0.0027623 | 0 |  | 0 | 0 | -0.0028637 | 0 |  | 0 | 0 | -0.0029565 | 0 |  | 0 | 0 | -0.0030418 | 0 |  | 0 | 0 | -0.0031205 | 0 |  | 0 | 0 | -0.0031933 | 0 |  | 0 | 0
36 |  | Concrete | 4 | 55.8 |  |  | -21.0992 | 176.2665 |  |  | 0.002349 | 2.0608 |  | 114.9952 | 20269.7944 |  | 0.0013929 | 2.4947 |  | 139.2025 | 24536.722 |  | 0.00065515 | 1.6352 |  | 91.246 | 16083.6099 |  | 6.8581e-05 | 0.20962 |  | 11.6966 | 2061.7101 |  | -0.00040895 | 0 |  | 0 | 0 | -0.00080525 | 0 |  | 0 | 0 | -0.0011394 | 0 |  | 0 | 0 | -0.001425 | 0 |  | 0 | 0 | -0.0016719 | 0 |  | 0 | 0 | -0.0018875 | 0 |  | 0 | 0 | -0.0020773 | 0 |  | 0 | 0 | -0.0022458 | 0 |  | 0 | 0 | -0.0023963 | 0 |  | 0 | 0 | -0.0025316 | 0 |  | 0 | 0 | -0.0026538 | 0 |  | 0 | 0 | -0.0027648 | 0 |  | 0 | 0 | -0.002866 | 0 |  | 0 | 0 | -0.0029588 | 0 |  | 0 | 0 | -0.003044 | 0 |  | 0 | 0 | -0.0031226 | 0 |  | 0 | 0 | -0.0031954 | 0 |  | 0 | 0
37 |  | Concrete | 5 | 55.8 |  |  | -16.3148 | 175.8806 |  |  | 0.002341 | 2.0718 |  | 115.6056 | 20332.7776 |  | 0.0013859 | 2.4914 |  | 139.02 | 24450.9205 |  | 0.00064894 | 1.6236 |  | 90.5962 | 15934.1168 |  | 6.3009e-05 | 0.19292 |  | 10.765 | 1893.3544 |  | -0.000414 | 0 |  | 0 | 0 | -0.00080988 | 0 |  | 0 | 0 | -0.0011437 | 0 |  | 0 | 0 | -0.001429 | 0 |  | 0 | 0 | -0.0016756 | 0 |  | 0 | 0 | -0.001891 | 0 |  | 0 | 0 | -0.0020806 | 0 |  | 0 | 0 | -0.0022489 | 0 |  | 0 | 0 | -0.0023992 | 0 |  | 0 | 0 | -0.0025343 | 0 |  | 0 | 0 | -0.0026564 | 0 |  | 0 | 0 | -0.0027673 | 0 |  | 0 | 0 | -0.0028684 | 0 |  | 0 | 0 | -0.0029611 | 0 |  | 0 | 0 | -0.0030462 | 0 |  | 0 | 0 | -0.0031247 | 0 |  | 0 | 0 | -0.0031974 | 0 |  | 0 | 0
38 |  | Concrete | 6 | 55.8 |  |  | -11.5303 | 175.4948 |  |  | 0.0023329 | 2.0826 |  | 116.209 | 20394.0785 |  | 0.0013789 | 2.488 |  | 138.8323 | 24364.3407 |  | 0.00064274 | 1.6119 |  | 89.9423 | 15784.4038 |  | 5.7437e-05 | 0.17617 |  | 9.8301 | 1725.1366 |  | -0.00041906 | 0 |  | 0 | 0 | -0.0008145 | 0 |  | 0 | 0 | -0.001148 | 0 |  | 0 | 0 | -0.0014329 | 0 |  | 0 | 0 | -0.0016793 | 0 |  | 0 | 0 | -0.0018944 | 0 |  | 0 | 0 | -0.0020838 | 0 |  | 0 | 0 | -0.0022519 | 0 |  | 0 | 0 | -0.0024021 | 0 |  | 0 | 0 | -0.0025371 | 0 |  | 0 | 0 | -0.002659 | 0 |  | 0 | 0 | -0.0027698 | 0 |  | 0 | 0 | -0.0028708 | 0 |  | 0 | 0 | -0.0029633 | 0 |  | 0 | 0 | -0.0030484 | 0 |  | 0 | 0 | -0.0031268 | 0 |  | 0 | 0 | -0.0031994 | 0 |  | 0 | 0
39 |  | Concrete | 7 | 55.8 |  |  | -6.7458 | 175.1089 |  |  | 0.0023249 | 2.0933 |  | 116.8056 | 20453.705 |  | 0.0013719 | 2.4846 |  | 138.6394 | 24276.9886 |  | 0.00063653 | 1.6001 |  | 89.2843 | 15634.4758 |  | 5.1865e-05 | 0.15935 |  | 8.892 | 1557.0604 |  | -0.00042411 | 0 |  | 0 | 0 | -0.00081913 | 0 |  | 0 | 0 | -0.0011522 | 0 |  | 0 | 0 | -0.0014369 | 0 |  | 0 | 0 | -0.001683 | 0 |  | 0 | 0 | -0.0018979 | 0 |  | 0 | 0 | -0.0020871 | 0 |  | 0 | 0 | -0.002255 | 0 |  | 0 | 0 | -0.002405 | 0 |  | 0 | 0 | -0.0025398 | 0 |  | 0 | 0 | -0.0026617 | 0 |  | 0 | 0 | -0.0027723 | 0 |  | 0 | 0 | -0.0028732 | 0 |  | 0 | 0 | -0.0029656 | 0 |  | 0 | 0 | -0.0030506 | 0 |  | 0 | 0 | -0.0031289 | 0 |  | 0 | 0 | -0.0032014 | 0 |  | 0 | 0
40 |  | Concrete | 8 | 55.8 |  |  | -1.9614 | 174.7231 |  |  | 0.0023168 | 2.1039 |  | 117.3953 | 20511.6652 |  | 0.0013649 | 2.481 |  | 138.4412 | 24188.8703 |  | 0.00063032 | 1.5882 |  | 88.6222 | 15484.3375 |  | 4.6294e-05 | 0.14248 |  | 7.9505 | 1389.1297 |  | -0.00042916 | 0 |  | 0 | 0 | -0.00082375 | 0 |  | 0 | 0 | -0.0011565 | 0 |  | 0 | 0 | -0.0014408 | 0 |  | 0 | 0 | -0.0016867 | 0 |  | 0 | 0 | -0.0019013 | 0 |  | 0 | 0 | -0.0020903 | 0 |  | 0 | 0 | -0.0022581 | 0 |  | 0 | 0 | -0.0024079 | 0 |  | 0 | 0 | -0.0025426 | 0 |  | 0 | 0 | -0.0026643 | 0 |  | 0 | 0 | -0.0027748 | 0 |  | 0 | 0 | -0.0028756 | 0 |  | 0 | 0 | -0.0029679 | 0 |  | 0 | 0 | -0.0030528 | 0 |  | 0 | 0 | -0.0031311 | 0 |  | 0 | 0 | -0.0032035 | 0 |  | 0 | 0
41 |  | Concrete | 9 | 55.8 |  |  | 2.8231 | 174.3372 |  |  | 0.0023088 | 2.1143 |  | 117.9781 | 20567.9671 |  | 0.0013579 | 2.4774 |  | 138.2378 | 24099.9917 |  | 0.00062411 | 1.5763 |  | 87.9559 | 15333.9936 |  | 4.0722e-05 | 0.12555 |  | 7.0057 | 1221.3484 |  | -0.00043422 | 0 |  | 0 | 0 | -0.00082837 | 0 |  | 0 | 0 | -0.0011607 | 0 |  | 0 | 0 | -0.0014448 | 0 |  | 0 | 0 | -0.0016904 | 0 |  | 0 | 0 | -0.0019048 | 0 |  | 0 | 0 | -0.0020936 | 0 |  | 0 | 0 | -0.0022611 | 0 |  | 0 | 0 | -0.0024108 | 0 |  | 0 | 0 | -0.0025453 | 0 |  | 0 | 0 | -0.0026669 | 0 |  | 0 | 0 | -0.0027773 | 0 |  | 0 | 0 | -0.002878 | 0 |  | 0 | 0 | -0.0029702 | 0 |  | 0 | 0 | -0.003055 | 0 |  | 0 | 0 | -0.0031332 | 0 |  | 0 | 0 | -0.0032055 | 0 |  | 0 | 0
42 |  | Concrete | 10 | 55.8 |  |  | 7.6076 | 173.9514 |  |  | 0.0023008 | 2.1246 |  | 118.5539 | 20622.6186 |  | 0.0013509 | 2.4736 |  | 138.0291 | 24010.3591 |  | 0.0006179 | 1.5643 |  | 87.2856 | 15183.4489 |  | 3.515e-05 | 0.10856 |  | 6.0576 | 1053.7203 |  | -0.00043927 | 0 |  | 0 | 0 | -0.000833 | 0 |  | 0 | 0 | -0.001165 | 0 |  | 0 | 0 | -0.0014488 | 0 |  | 0 | 0 | -0.001694 | 0 |  | 0 | 0 | -0.0019082 | 0 |  | 0 | 0 | -0.0020968 | 0 |  | 0 | 0 | -0.0022642 | 0 |  | 0 | 0 | -0.0024137 | 0 |  | 0 | 0 | -0.0025481 | 0 |  | 0 | 0 | -0.0026695 | 0 |  | 0 | 0 | -0.0027798 | 0 |  | 0 | 0 | -0.0028804 | 0 |  | 0 | 0 | -0.0029725 | 0 |  | 0 | 0 | -0.0030572 | 0 |  | 0 | 0 | -0.0031353 | 0 |  | 0 | 0 | -0.0032075 | 0 |  | 0 | 0
43 |  | Concrete | 11 | 27.9 |  |  | 40.7001 | 171.2826 |  |  | 0.0022451 | 2.1926 |  | 61.174 | 10478.0455 |  | 0.0013024 | 2.4452 |  | 68.2213 | 11685.1234 |  | 0.00057497 | 1.4791 |  | 41.2683 | 7068.5357 |  | -3.3881e-06 | 0 |  | 0 | 0 |  | -0.00047423 | 0 |  | 0 | 0 | -0.00086498 | 0 |  | 0 | 0 | -0.0011945 | 0 |  | 0 | 0 | -0.0014761 | 0 |  | 0 | 0 | -0.0017195 | 0 |  | 0 | 0 | -0.0019321 | 0 |  | 0 | 0 | -0.0021193 | 0 |  | 0 | 0 | -0.0022854 | 0 |  | 0 | 0 | -0.0024337 | 0 |  | 0 | 0 | -0.0025671 | 0 |  | 0 | 0 | -0.0026876 | 0 |  | 0 | 0 | -0.0027971 | 0 |  | 0 | 0 | -0.0028969 | 0 |  | 0 | 0 | -0.0029883 | 0 |  | 0 | 0 | -0.0030724 | 0 |  | 0 | 0 | -0.0031499 | 0 |  | 0 | 0 | -0.0032216 | 0 |  | 0 | 0
44 |  | Concrete | 12 | 27.9 |  |  | 38.3079 | 171.4756 |  |  | 0.0022491 | 2.1879 |  | 61.0424 | 10467.2811 |  | 0.0013059 | 2.4474 |  | 68.2828 | 11708.8384 |  | 0.00057807 | 1.4854 |  | 41.4432 | 7106.4969 |  | -6.022e-07 | 0 |  | 0 | 0 |  | -0.0004717 | 0 |  | 0 | 0 | -0.00086267 | 0 |  | 0 | 0 | -0.0011924 | 0 |  | 0 | 0 | -0.0014741 | 0 |  | 0 | 0 | -0.0017177 | 0 |  | 0 | 0 | -0.0019304 | 0 |  | 0 | 0 | -0.0021176 | 0 |  | 0 | 0 | -0.0022838 | 0 |  | 0 | 0 | -0.0024323 | 0 |  | 0 | 0 | -0.0025657 | 0 |  | 0 | 0 | -0.0026863 | 0 |  | 0 | 0 | -0.0027958 | 0 |  | 0 | 0 | -0.0028957 | 0 |  | 0 | 0 | -0.0029872 | 0 |  | 0 | 0 | -0.0030713 | 0 |  | 0 | 0 | -0.0031488 | 0 |  | 0 | 0 | -0.0032206 | 0 |  | 0 | 0
45 |  | Concrete | 13 | 27.9 |  |  | 35.9157 | 171.6685 |  |  | 0.0022532 | 2.1832 |  | 60.9099 | 10456.3179 |  | 0.0013094 | 2.4496 |  | 68.3437 | 11732.4647 |  | 0.00058117 | 1.4917 |  | 41.6176 | 7144.4373 |  | 2.1837e-06 | 0.006813 |  | 0.19008 | 32.631 |  | -0.00046917 | 0 |  | 0 | 0 | -0.00086036 | 0 |  | 0 | 0 | -0.0011902 | 0 |  | 0 | 0 | -0.0014721 | 0 |  | 0 | 0 | -0.0017158 | 0 |  | 0 | 0 | -0.0019286 | 0 |  | 0 | 0 | -0.002116 | 0 |  | 0 | 0 | -0.0022823 | 0 |  | 0 | 0 | -0.0024308 | 0 |  | 0 | 0 | -0.0025644 | 0 |  | 0 | 0 | -0.002685 | 0 |  | 0 | 0 | -0.0027946 | 0 |  | 0 | 0 | -0.0028945 | 0 |  | 0 | 0 | -0.002986 | 0 |  | 0 | 0 | -0.0030702 | 0 |  | 0 | 0 | -0.0031478 | 0 |  | 0 | 0 | -0.0032196 | 0 |  | 0 | 0
46 |  | Concrete | 14 | 27.9 |  |  | 33.5234 | 171.8614 |  |  | 0.0022572 | 2.1784 |  | 60.7766 | 10445.1552 |  | 0.0013129 | 2.4518 |  | 68.404 | 11756.002 |  | 0.00058428 | 1.4979 |  | 41.7916 | 7182.3568 |  | 4.9696e-06 | 0.015492 |  | 0.43221 | 74.2808 |  | -0.00046665 | 0 |  | 0 | 0 | -0.00085805 | 0 |  | 0 | 0 | -0.0011881 | 0 |  | 0 | 0 | -0.0014702 | 0 |  | 0 | 0 | -0.001714 | 0 |  | 0 | 0 | -0.0019269 | 0 |  | 0 | 0 | -0.0021144 | 0 |  | 0 | 0 | -0.0022808 | 0 |  | 0 | 0 | -0.0024294 | 0 |  | 0 | 0 | -0.002563 | 0 |  | 0 | 0 | -0.0026837 | 0 |  | 0 | 0 | -0.0027933 | 0 |  | 0 | 0 | -0.0028933 | 0 |  | 0 | 0 | -0.0029849 | 0 |  | 0 | 0 | -0.0030691 | 0 |  | 0 | 0 | -0.0031467 | 0 |  | 0 | 0 | -0.0032185 | 0 |  | 0 | 0
47 |  | Concrete | 15 | 27.9 |  |  | 31.1312 | 172.0543 |  |  | 0.0022612 | 2.1736 |  | 60.6424 | 10433.7926 |  | 0.0013164 | 2.4539 |  | 68.4636 | 11779.4499 |  | 0.00058738 | 1.5041 |  | 41.965 | 7220.255 |  | 7.7555e-06 | 0.024155 |  | 0.67393 | 115.9527 |  | -0.00046412 | 0 |  | 0 | 0 | -0.00085573 | 0 |  | 0 | 0 | -0.001186 | 0 |  | 0 | 0 | -0.0014682 | 0 |  | 0 | 0 | -0.0017122 | 0 |  | 0 | 0 | -0.0019252 | 0 |  | 0 | 0 | -0.0021128 | 0 |  | 0 | 0 | -0.0022792 | 0 |  | 0 | 0 | -0.002428 | 0 |  | 0 | 0 | -0.0025616 | 0 |  | 0 | 0 | -0.0026824 | 0 |  | 0 | 0 | -0.0027921 | 0 |  | 0 | 0 | -0.0028921 | 0 |  | 0 | 0 | -0.0029838 | 0 |  | 0 | 0 | -0.003068 | 0 |  | 0 | 0 | -0.0031457 | 0 |  | 0 | 0 | -0.0032175 | 0 |  | 0 | 0
48 |  | Concrete | 16 | 27.9 |  |  | 28.739 | 172.2472 |  |  | 0.0022652 | 2.1687 |  | 60.5074 | 10422.2297 |  | 0.0013199 | 2.456 |  | 68.5225 | 11802.8081 |  | 0.00059049 | 1.5103 |  | 42.1379 | 7258.1316 |  | 1.0541e-05 | 0.032804 |  | 0.91523 | 157.6466 |  | -0.00046159 | 0 |  | 0 | 0 | -0.00085342 | 0 |  | 0 | 0 | -0.0011838 | 0 |  | 0 | 0 | -0.0014662 | 0 |  | 0 | 0 | -0.0017103 | 0 |  | 0 | 0 | -0.0019235 | 0 |  | 0 | 0 | -0.0021111 | 0 |  | 0 | 0 | -0.0022777 | 0 |  | 0 | 0 | -0.0024265 | 0 |  | 0 | 0 | -0.0025602 | 0 |  | 0 | 0 | -0.0026811 | 0 |  | 0 | 0 | -0.0027908 | 0 |  | 0 | 0 | -0.0028909 | 0 |  | 0 | 0 | -0.0029826 | 0 |  | 0 | 0 | -0.0030669 | 0 |  | 0 | 0 | -0.0031446 | 0 |  | 0 | 0 | -0.0032165 | 0 |  | 0 | 0
49 |  | Concrete | 17 | 27.9 |  |  | 26.3467 | 172.4402 |  |  | 0.0022692 | 2.1639 |  | 60.3715 | 10410.4659 |  | 0.0013234 | 2.4581 |  | 68.5808 | 11826.076 |  | 0.00059359 | 1.5165 |  | 42.3102 | 7295.9864 |  | 1.3327e-05 | 0.041438 |  | 1.1561 | 199.3623 |  | -0.00045907 | 0 |  | 0 | 0 | -0.00085111 | 0 |  | 0 | 0 | -0.0011817 | 0 |  | 0 | 0 | -0.0014642 | 0 |  | 0 | 0 | -0.0017085 | 0 |  | 0 | 0 | -0.0019217 | 0 |  | 0 | 0 | -0.0021095 | 0 |  | 0 | 0 | -0.0022762 | 0 |  | 0 | 0 | -0.0024251 | 0 |  | 0 | 0 | -0.0025589 | 0 |  | 0 | 0 | -0.0026798 | 0 |  | 0 | 0 | -0.0027896 | 0 |  | 0 | 0 | -0.0028897 | 0 |  | 0 | 0 | -0.0029815 | 0 |  | 0 | 0 | -0.0030658 | 0 |  | 0 | 0 | -0.0031435 | 0 |  | 0 | 0 | -0.0032155 | 0 |  | 0 | 0
50 |  | Concrete | 18 | 27.9 |  |  | 23.9545 | 172.6331 |  |  | 0.0022733 | 2.1589 |  | 60.2347 | 10398.5007 |  | 0.0013269 | 2.4602 |  | 68.6384 | 11849.2535 |  | 0.00059669 | 1.5227 |  | 42.4821 | 7333.8189 |  | 1.6113e-05 | 0.050057 |  | 1.3966 | 241.0995 |  | -0.00045654 | 0 |  | 0 | 0 | -0.0008488 | 0 |  | 0 | 0 | -0.0011796 | 0 |  | 0 | 0 | -0.0014623 | 0 |  | 0 | 0 | -0.0017066 | 0 |  | 0 | 0 | -0.00192 | 0 |  | 0 | 0 | -0.0021079 | 0 |  | 0 | 0 | -0.0022746 | 0 |  | 0 | 0 | -0.0024236 | 0 |  | 0 | 0 | -0.0025575 | 0 |  | 0 | 0 | -0.0026785 | 0 |  | 0 | 0 | -0.0027883 | 0 |  | 0 | 0 | -0.0028885 | 0 |  | 0 | 0 | -0.0029803 | 0 |  | 0 | 0 | -0.0030647 | 0 |  | 0 | 0 | -0.0031425 | 0 |  | 0 | 0 | -0.0032145 | 0 |  | 0 | 0
51 |  | Concrete | 19 | 27.9 |  |  | 21.5623 | 172.826 |  |  | 0.0022773 | 2.154 |  | 60.0971 | 10386.3336 |  | 0.0013304 | 2.4622 |  | 68.6953 | 11872.34 |  | 0.0005998 | 1.5288 |  | 42.6535 | 7371.629 |  | 1.8899e-05 | 0.058662 |  | 1.6367 | 282.8579 |  | -0.00045401 | 0 |  | 0 | 0 | -0.00084649 | 0 |  | 0 | 0 | -0.0011774 | 0 |  | 0 | 0 | -0.0014603 | 0 |  | 0 | 0 | -0.0017048 | 0 |  | 0 | 0 | -0.0019183 | 0 |  | 0 | 0 | -0.0021063 | 0 |  | 0 | 0 | -0.0022731 | 0 |  | 0 | 0 | -0.0024222 | 0 |  | 0 | 0 | -0.0025561 | 0 |  | 0 | 0 | -0.0026772 | 0 |  | 0 | 0 | -0.0027871 | 0 |  | 0 | 0 | -0.0028874 | 0 |  | 0 | 0 | -0.0029792 | 0 |  | 0 | 0 | -0.0030636 | 0 |  | 0 | 0 | -0.0031414 | 0 |  | 0 | 0 | -0.0032135 | 0 |  | 0 | 0
52 |  | Concrete | 20 | 27.9 |  |  | 19.17 | 173.0189 |  |  | 0.0022813 | 2.1491 |  | 59.9585 | 10373.9641 |  | 0.0013339 | 2.4642 |  | 68.7516 | 11895.3352 |  | 0.0006029 | 1.5349 |  | 42.8243 | 7409.4163 |  | 2.1685e-05 | 0.067251 |  | 1.8763 | 324.6374 |  | -0.00045148 | 0 |  | 0 | 0 | -0.00084417 | 0 |  | 0 | 0 | -0.0011753 | 0 |  | 0 | 0 | -0.0014583 | 0 |  | 0 | 0 | -0.001703 | 0 |  | 0 | 0 | -0.0019165 | 0 |  | 0 | 0 | -0.0021047 | 0 |  | 0 | 0 | -0.0022716 | 0 |  | 0 | 0 | -0.0024207 | 0 |  | 0 | 0 | -0.0025547 | 0 |  | 0 | 0 | -0.0026759 | 0 |  | 0 | 0 | -0.0027858 | 0 |  | 0 | 0 | -0.0028862 | 0 |  | 0 | 0 | -0.002978 | 0 |  | 0 | 0 | -0.0030625 | 0 |  | 0 | 0 | -0.0031404 | 0 |  | 0 | 0 | -0.0032125 | 0 |  | 0 | 0
53 |  | Concrete | 21 | 32 |  |  | 14.3084 | 177.424 |  |  | 0.0023732 | 2.0273 |  | 64.8732 | 11510.0624 |  | 0.001414 | 2.5039 |  | 80.1252 | 14216.1408 |  | 0.00067377 | 1.6697 |  | 53.4312 | 9479.9844 |  | 8.5296e-05 | 0.25934 |  | 8.299 | 1472.4394 |  | -0.00039379 | 0 |  | 0 | 0 | -0.00079138 | 0 |  | 0 | 0 | -0.0011267 | 0 |  | 0 | 0 | -0.0014132 | 0 |  | 0 | 0 | -0.0016609 | 0 |  | 0 | 0 | -0.0018772 | 0 |  | 0 | 0 | -0.0020676 | 0 |  | 0 | 0 | -0.0022366 | 0 |  | 0 | 0 | -0.0023876 | 0 |  | 0 | 0 | -0.0025233 | 0 |  | 0 | 0 | -0.0026459 | 0 |  | 0 | 0 | -0.0027573 | 0 |  | 0 | 0 | -0.0028589 | 0 |  | 0 | 0 | -0.0029519 | 0 |  | 0 | 0 | -0.0030374 | 0 |  | 0 | 0 | -0.0031163 | 0 |  | 0 | 0 | -0.0031893 | 0 |  | 0 | 0
54 |  | Concrete | 22 | 32 |  |  | 13.9868 | 173.4369 |  |  | 0.00229 | 2.1382 |  | 68.4221 | 11866.9155 |  | 0.0013415 | 2.4685 |  | 78.9923 | 13700.1785 |  | 0.00060963 | 1.5481 |  | 49.54 | 8592.068 |  | 2.7721e-05 | 0.085811 |  | 2.746 | 476.2501 |  | -0.00044601 | 0 |  | 0 | 0 | -0.00083916 | 0 |  | 0 | 0 | -0.0011707 | 0 |  | 0 | 0 | -0.001454 | 0 |  | 0 | 0 | -0.001699 | 0 |  | 0 | 0 | -0.0019128 | 0 |  | 0 | 0 | -0.0021011 | 0 |  | 0 | 0 | -0.0022683 | 0 |  | 0 | 0 | -0.0024176 | 0 |  | 0 | 0 | -0.0025518 | 0 |  | 0 | 0 | -0.002673 | 0 |  | 0 | 0 | -0.0027831 | 0 |  | 0 | 0 | -0.0028836 | 0 |  | 0 | 0 | -0.0029756 | 0 |  | 0 | 0 | -0.0030601 | 0 |  | 0 | 0 | -0.0031381 | 0 |  | 0 | 0 | -0.0032103 | 0 |  | 0 | 0
55 |  | Concrete | 23 | 32 |  |  | 13.6653 | 169.4499 |  |  | 0.0022069 | 2.2359 |  | 71.5483 | 12123.8518 |  | 0.0012691 | 2.4231 |  | 77.5386 | 13138.9047 |  | 0.00054548 | 1.4187 |  | 45.3971 | 7692.536 |  | -2.9854e-05 | 0 |  | 0 | 0 |  | -0.00049823 | 0 |  | 0 | 0 | -0.00088695 | 0 |  | 0 | 0 | -0.0012147 | 0 |  | 0 | 0 | -0.0014949 | 0 |  | 0 | 0 | -0.001737 | 0 |  | 0 | 0 | -0.0019485 | 0 |  | 0 | 0 | -0.0021347 | 0 |  | 0 | 0 | -0.0022999 | 0 |  | 0 | 0 | -0.0024475 | 0 |  | 0 | 0 | -0.0025802 | 0 |  | 0 | 0 | -0.0027001 | 0 |  | 0 | 0 | -0.002809 | 0 |  | 0 | 0 | -0.0029083 | 0 |  | 0 | 0 | -0.0029992 | 0 |  | 0 | 0 | -0.0030828 | 0 |  | 0 | 0 | -0.0031599 | 0 |  | 0 | 0 | -0.0032312 | 0 |  | 0 | 0
56 |  | Concrete | 24 | 32 |  |  | 13.3438 | 165.4628 |  |  | 0.0021238 | 2.3204 |  | 74.2519 | 12285.9266 |  | 0.0011967 | 2.3676 |  | 75.7642 | 12536.1554 |  | 0.00048133 | 1.2813 |  | 41.0026 | 6784.3986 |  | -8.7429e-05 | 0 |  | 0 | 0 |  | -0.00055046 | 0 |  | 0 | 0 | -0.00093473 | 0 |  | 0 | 0 | -0.0012588 | 0 |  | 0 | 0 | -0.0015357 | 0 |  | 0 | 0 | -0.0017751 | 0 |  | 0 | 0 | -0.0019841 | 0 |  | 0 | 0 | -0.0021682 | 0 |  | 0 | 0 | -0.0023315 | 0 |  | 0 | 0 | -0.0024775 | 0 |  | 0 | 0 | -0.0026086 | 0 |  | 0 | 0 | -0.0027271 | 0 |  | 0 | 0 | -0.0028348 | 0 |  | 0 | 0 | -0.0029329 | 0 |  | 0 | 0 | -0.0030228 | 0 |  | 0 | 0 | -0.0031055 | 0 |  | 0 | 0 | -0.0031817 | 0 |  | 0 | 0 | -0.0032522 | 0 |  | 0 | 0
57 |  | Concrete | 25 | 62.525 |  |  | 12.8534 | 159.3826 |  |  | 0.001997 | 2.4238 |  | 151.5472 | 24153.9723 |  | 0.0010863 | 2.2638 |  | 141.5424 | 22559.3873 |  | 0.0003835 | 1.0568 |  | 66.0739 | 10531.0287 |  | -0.00017523 | 0 |  | 0 | 0 |  | -0.0006301 | 0 |  | 0 | 0 | -0.0010076 | 0 |  | 0 | 0 | -0.0013259 | 0 |  | 0 | 0 | -0.001598 | 0 |  | 0 | 0 | -0.0018332 | 0 |  | 0 | 0 | -0.0020385 | 0 |  | 0 | 0 | -0.0022193 | 0 |  | 0 | 0 | -0.0023798 | 0 |  | 0 | 0 | -0.0025231 | 0 |  | 0 | 0 | -0.002652 | 0 |  | 0 | 0 | -0.0027684 | 0 |  | 0 | 0 | -0.0028742 | 0 |  | 0 | 0 | -0.0029706 | 0 |  | 0 | 0 | -0.0030589 | 0 |  | 0 | 0 | -0.0031401 | 0 |  | 0 | 0 | -0.003215 | 0 |  | 0 | 0 | -0.0032843 | 0 |  | 0 | 0
58 |  | Concrete | 26 | 62.525 |  |  | 12.1943 | 151.2091 |  |  | 0.0018266 | 2.5144 |  | 157.2129 | 23772.0271 |  | 0.00093781 | 2.0874 |  | 130.5168 | 19735.3275 |  | 0.000252 | 0.72606 |  | 45.3969 | 6864.4255 |  | -0.00029326 | 0 |  | 0 | 0 |  | -0.00073716 | 0 |  | 0 | 0 | -0.0011055 | 0 |  | 0 | 0 | -0.0014162 | 0 |  | 0 | 0 | -0.0016817 | 0 |  | 0 | 0 | -0.0019112 | 0 |  | 0 | 0 | -0.0021116 | 0 |  | 0 | 0 | -0.0022881 | 0 |  | 0 | 0 | -0.0024446 | 0 |  | 0 | 0 | -0.0025845 | 0 |  | 0 | 0 | -0.0027103 | 0 |  | 0 | 0 | -0.0028239 | 0 |  | 0 | 0 | -0.0029271 | 0 |  | 0 | 0 | -0.0030212 | 0 |  | 0 | 0 | -0.0031074 | 0 |  | 0 | 0 | -0.0031866 | 0 |  | 0 | 0 | -0.0032597 | 0 |  | 0 | 0 | -0.0033273 | 0 |  | 0 | 0
59 |  | Concrete | 27 | 62.525 |  |  | 11.5351 | 143.0356 |  |  | 0.0016561 | 2.5495 |  | 159.4083 | 22801.0599 |  | 0.00078936 | 1.869 |  | 116.8577 | 16714.8139 |  | 0.00012049 | 0.36231 |  | 22.6534 | 3240.2445 |  | -0.00041129 | 0 |  | 0 | 0 |  | -0.00084421 | 0 |  | 0 | 0 | -0.0012035 | 0 |  | 0 | 0 | -0.0015065 | 0 |  | 0 | 0 | -0.0017654 | 0 |  | 0 | 0 | -0.0019892 | 0 |  | 0 | 0 | -0.0021847 | 0 |  | 0 | 0 | -0.0023568 | 0 |  | 0 | 0 | -0.0025095 | 0 |  | 0 | 0 | -0.0026459 | 0 |  | 0 | 0 | -0.0027686 | 0 |  | 0 | 0 | -0.0028794 | 0 |  | 0 | 0 | -0.00298 | 0 |  | 0 | 0 | -0.0030718 | 0 |  | 0 | 0 | -0.0031559 | 0 |  | 0 | 0 | -0.0032331 | 0 |  | 0 | 0 | -0.0033044 | 0 |  | 0 | 0 | -0.0033704 | 0 |  | 0 | 0
60 |  | Concrete | 28 | 62.525 |  |  | 10.876 | 134.8622 |  |  | 0.0014857 | 2.5291 |  | 158.1331 | 21326.1685 |  | 0.0006409 | 1.6084 |  | 100.5651 | 13562.4215 |  | -1.1011e-05 | 0 |  | 0 | 0 |  | -0.00052932 | 0 |  | 0 | 0 |  | -0.00095127 | 0 |  | 0 | 0 | -0.0013015 | 0 |  | 0 | 0 | -0.0015967 | 0 |  | 0 | 0 | -0.0018491 | 0 |  | 0 | 0 | -0.0020673 | 0 |  | 0 | 0 | -0.0022578 | 0 |  | 0 | 0 | -0.0024255 | 0 |  | 0 | 0 | -0.0025744 | 0 |  | 0 | 0 | -0.0027073 | 0 |  | 0 | 0 | -0.0028269 | 0 |  | 0 | 0 | -0.0029349 | 0 |  | 0 | 0 | -0.003033 | 0 |  | 0 | 0 | -0.0031224 | 0 |  | 0 | 0 | -0.0032043 | 0 |  | 0 | 0 | -0.0032797 | 0 |  | 0 | 0 | -0.0033491 | 0 |  | 0 | 0 | -0.0034134 | 0 |  | 0 | 0
61 |  | Concrete | 29 | 62.525 |  |  | 10.2168 | 126.6887 |  |  | 0.0013153 | 2.4532 |  | 153.3874 | 19432.4505 |  | 0.00049245 | 1.3057 |  | 81.6389 | 10342.7255 |  | -0.00014252 | 0 |  | 0 | 0 |  | -0.00064735 | 0 |  | 0 | 0 |  | -0.0010583 | 0 |  | 0 | 0 | -0.0013994 | 0 |  | 0 | 0 | -0.001687 | 0 |  | 0 | 0 | -0.0019328 | 0 |  | 0 | 0 | -0.0021453 | 0 |  | 0 | 0 | -0.0023309 | 0 |  | 0 | 0 | -0.0024942 | 0 |  | 0 | 0 | -0.0026392 | 0 |  | 0 | 0 | -0.0027687 | 0 |  | 0 | 0 | -0.0028852 | 0 |  | 0 | 0 | -0.0029904 | 0 |  | 0 | 0 | -0.0030859 | 0 |  | 0 | 0 | -0.003173 | 0 |  | 0 | 0 | -0.0032528 | 0 |  | 0 | 0 | -0.0033262 | 0 |  | 0 | 0 | -0.0033938 | 0 |  | 0 | 0 | -0.0034564 | 0 |  | 0 | 0
62 |  | Concrete | 30 | 62.525 |  |  | 9.5577 | 118.5152 |  |  | 0.0011449 | 2.3218 |  | 145.1712 | 17205.0037 |  | 0.000344 | 0.96088 |  | 60.0792 | 7120.3011 |  | -0.00027402 | 0 |  | 0 | 0 |  | -0.00076537 | 0 |  | 0 | 0 |  | -0.0011654 | 0 |  | 0 | 0 | -0.0014974 | 0 |  | 0 | 0 | -0.0017773 | 0 |  | 0 | 0 | -0.0020165 | 0 |  | 0 | 0 | -0.0022234 | 0 |  | 0 | 0 | -0.0024039 | 0 |  | 0 | 0 | -0.002563 | 0 |  | 0 | 0 | -0.0027041 | 0 |  | 0 | 0 | -0.0028301 | 0 |  | 0 | 0 | -0.0029435 | 0 |  | 0 | 0 | -0.0030458 | 0 |  | 0 | 0 | -0.0031388 | 0 |  | 0 | 0 | -0.0032236 | 0 |  | 0 | 0 | -0.0033013 | 0 |  | 0 | 0 | -0.0033727 | 0 |  | 0 | 0 | -0.0034386 | 0 |  | 0 | 0 | -0.0034995 | 0 |  | 0 | 0
63 |  | Concrete | 31 | 62.525 |  |  | 8.8985 | 110.3418 |  |  | 0.00097447 | 2.1349 |  | 133.4846 | 14728.926 |  | 0.00019554 | 0.57395 |  | 35.886 | 3959.7233 |  | -0.00040552 | 0 |  | 0 | 0 |  | -0.0008834 | 0 |  | 0 | 0 |  | -0.0012724 | 0 |  | 0 | 0 | -0.0015953 | 0 |  | 0 | 0 | -0.0018676 | 0 |  | 0 | 0 | -0.0021003 | 0 |  | 0 | 0 | -0.0023014 | 0 |  | 0 | 0 | -0.002477 | 0 |  | 0 | 0 | -0.0026317 | 0 |  | 0 | 0 | -0.0027689 | 0 |  | 0 | 0 | -0.0028915 | 0 |  | 0 | 0 | -0.0030018 | 0 |  | 0 | 0 | -0.0031013 | 0 |  | 0 | 0 | -0.0031918 | 0 |  | 0 | 0 | -0.0032742 | 0 |  | 0 | 0 | -0.0033498 | 0 |  | 0 | 0 | -0.0034192 | 0 |  | 0 | 0 | -0.0034833 | 0 |  | 0 | 0 | -0.0035425 | 0 |  | 0 | 0
64 |  | Concrete | 32 | 62.525 |  |  | 8.2394 | 102.1683 |  |  | 0.00080405 | 1.8925 |  | 118.3275 | 12089.3151 |  | 4.7088e-05 | 0.14489 |  | 9.0592 | 925.5672 |  | -0.00053703 | 0 |  | 0 | 0 |  | -0.0010014 | 0 |  | 0 | 0 |  | -0.0013795 | 0 |  | 0 | 0 | -0.0016933 | 0 |  | 0 | 0 | -0.0019579 | 0 |  | 0 | 0 | -0.002184 | 0 |  | 0 | 0 | -0.0023795 | 0 |  | 0 | 0 | -0.0025501 | 0 |  | 0 | 0 | -0.0027004 | 0 |  | 0 | 0 | -0.0028338 | 0 |  | 0 | 0 | -0.002953 | 0 |  | 0 | 0 | -0.00306 | 0 |  | 0 | 0 | -0.0031568 | 0 |  | 0 | 0 | -0.0032447 | 0 |  | 0 | 0 | -0.0033249 | 0 |  | 0 | 0 | -0.0033983 | 0 |  | 0 | 0 | -0.0034657 | 0 |  | 0 | 0 | -0.003528 | 0 |  | 0 | 0 | -0.0035856 | 0 |  | 0 | 0
65 |  | Concrete | 33 | 62.525 |  |  | 7.5802 | 93.9948 |  |  | 0.00063364 | 1.5946 |  | 99.6998 | 9371.2688 |  | -0.00010137 | 0 |  | 0 | 0 |  | -0.00066853 | 0 |  | 0 | 0 |  | -0.0011195 | 0 |  | 0 | 0 |  | -0.0014866 | 0 |  | 0 | 0 | -0.0017912 | 0 |  | 0 | 0 | -0.0020481 | 0 |  | 0 | 0 | -0.0022677 | 0 |  | 0 | 0 | -0.0024575 | 0 |  | 0 | 0 | -0.0026232 | 0 |  | 0 | 0 | -0.0027692 | 0 |  | 0 | 0 | -0.0028987 | 0 |  | 0 | 0 | -0.0030144 | 0 |  | 0 | 0 | -0.0031183 | 0 |  | 0 | 0 | -0.0032123 | 0 |  | 0 | 0 | -0.0032976 | 0 |  | 0 | 0 | -0.0033755 | 0 |  | 0 | 0 | -0.0034467 | 0 |  | 0 | 0 | -0.0035123 | 0 |  | 0 | 0 | -0.0035727 | 0 |  | 0 | 0 | -0.0036286 | 0 |  | 0 | 0
66 |  | Concrete | 34 | 62.525 |  |  | 6.9211 | 85.8214 |  |  | 0.00046322 | 1.2411 |  | 77.6017 | 6659.8848 |  | -0.00024982 | 0 |  | 0 | 0 |  | -0.00080004 | 0 |  | 0 | 0 |  | -0.0012375 | 0 |  | 0 | 0 |  | -0.0015936 | 0 |  | 0 | 0 | -0.0018892 | 0 |  | 0 | 0 | -0.0021384 | 0 |  | 0 | 0 | -0.0023514 | 0 |  | 0 | 0 | -0.0025355 | 0 |  | 0 | 0 | -0.0026963 | 0 |  | 0 | 0 | -0.0028379 | 0 |  | 0 | 0 | -0.0029635 | 0 |  | 0 | 0 | -0.0030758 | 0 |  | 0 | 0 | -0.0031766 | 0 |  | 0 | 0 | -0.0032678 | 0 |  | 0 | 0 | -0.0033506 | 0 |  | 0 | 0 | -0.0034261 | 0 |  | 0 | 0 | -0.0034952 | 0 |  | 0 | 0 | -0.0035588 | 0 |  | 0 | 0 | -0.0036174 | 0 |  | 0 | 0 | -0.0036717 | 0 |  | 0 | 0
67 |  | Concrete | 35 | 62.525 |  |  | 6.2619 | 77.6479 |  |  | 0.0002928 | 0.8322 |  | 52.0331 | 4040.261 |  | -0.00039827 | 0 |  | 0 | 0 |  | -0.00093154 | 0 |  | 0 | 0 |  | -0.0013555 | 0 |  | 0 | 0 |  | -0.0017007 | 0 |  | 0 | 0 | -0.0019871 | 0 |  | 0 | 0 | -0.0022287 | 0 |  | 0 | 0 | -0.0024351 | 0 |  | 0 | 0 | -0.0026136 | 0 |  | 0 | 0 | -0.0027694 | 0 |  | 0 | 0 | -0.0029066 | 0 |  | 0 | 0 | -0.0030284 | 0 |  | 0 | 0 | -0.0031372 | 0 |  | 0 | 0 | -0.0032349 | 0 |  | 0 | 0 | -0.0033233 | 0 |  | 0 | 0 | -0.0034035 | 0 |  | 0 | 0 | -0.0034767 | 0 |  | 0 | 0 | -0.0035437 | 0 |  | 0 | 0 | -0.0036053 | 0 |  | 0 | 0 | -0.0036621 | 0 |  | 0 | 0 | -0.0037147 | 0 |  | 0 | 0
68 |  | Concrete | 36 | 62.525 |  |  | 5.6028 | 69.4744 |  |  | 0.00012238 | 0.36776 |  | 22.994 | 1597.495 |  | -0.00054673 | 0 |  | 0 | 0 |  | -0.001063 | 0 |  | 0 | 0 |  | -0.0014735 | 0 |  | 0 | 0 |  | -0.0018077 | 0 |  | 0 | 0 | -0.0020851 | 0 |  | 0 | 0 | -0.002319 | 0 |  | 0 | 0 | -0.0025188 | 0 |  | 0 | 0 | -0.0026916 | 0 |  | 0 | 0 | -0.0028425 | 0 |  | 0 | 0 | -0.0029753 | 0 |  | 0 | 0 | -0.0030932 | 0 |  | 0 | 0 | -0.0031986 | 0 |  | 0 | 0 | -0.0032932 | 0 |  | 0 | 0 | -0.0033788 | 0 |  | 0 | 0 | -0.0034564 | 0 |  | 0 | 0 | -0.0035273 | 0 |  | 0 | 0 | -0.0035922 | 0 |  | 0 | 0 | -0.0036518 | 0 |  | 0 | 0 | -0.0037068 | 0 |  | 0 | 0 | -0.0037577 | 0 |  | 0 | 0
69 |  | Concrete | 37 | 62.525 |  |  | 4.9436 | 61.301 |  |  | -4.804e-05 | 0 |  | 0 | 0 |  | -0.00069518 | 0 |  | 0 | 0 |  | -0.0011946 | 0 |  | 0 | 0 |  | -0.0015916 | 0 |  | 0 | 0 |  | -0.0019148 | 0 |  | 0 | 0 | -0.002183 | 0 |  | 0 | 0 | -0.0024092 | 0 |  | 0 | 0 | -0.0026025 | 0 |  | 0 | 0 | -0.0027697 | 0 |  | 0 | 0 | -0.0029156 | 0 |  | 0 | 0 | -0.0030441 | 0 |  | 0 | 0 | -0.0031581 | 0 |  | 0 | 0 | -0.00326 | 0 |  | 0 | 0 | -0.0033515 | 0 |  | 0 | 0 | -0.0034342 | 0 |  | 0 | 0 | -0.0035094 | 0 |  | 0 | 0 | -0.0035779 | 0 |  | 0 | 0 | -0.0036407 | 0 |  | 0 | 0 | -0.0036984 | 0 |  | 0 | 0 | -0.0037516 | 0 |  | 0 | 0 | -0.0038008 | 0 |  | 0 | 0
70 |  | Concrete | 38 | 62.525 |  |  | 4.2845 | 53.1275 |  |  | -0.00021846 | 0 |  | 0 | 0 |  | -0.00084364 | 0 |  | 0 | 0 |  | -0.0013261 | 0 |  | 0 | 0 |  | -0.0017096 | 0 |  | 0 | 0 |  | -0.0020219 | 0 |  | 0 | 0 | -0.002281 | 0 |  | 0 | 0 | -0.0024995 | 0 |  | 0 | 0 | -0.0026863 | 0 |  | 0 | 0 | -0.0028477 | 0 |  | 0 | 0 | -0.0029887 | 0 |  | 0 | 0 | -0.0031128 | 0 |  | 0 | 0 | -0.0032229 | 0 |  | 0 | 0 | -0.0033214 | 0 |  | 0 | 0 | -0.0034098 | 0 |  | 0 | 0 | -0.0034897 | 0 |  | 0 | 0 | -0.0035623 | 0 |  | 0 | 0 | -0.0036285 | 0 |  | 0 | 0 | -0.0036891 | 0 |  | 0 | 0 | -0.0037449 | 0 |  | 0 | 0 | -0.0037963 | 0 |  | 0 | 0 | -0.0038438 | 0 |  | 0 | 0
71 |  | Concrete | 39 | 62.525 |  |  | 3.6253 | 44.9541 |  |  | -0.00038888 | 0 |  | 0 | 0 |  | -0.00099209 | 0 |  | 0 | 0 |  | -0.0014576 | 0 |  | 0 | 0 |  | -0.0018276 | 0 |  | 0 | 0 |  | -0.0021289 | 0 |  | 0 | 0 | -0.0023789 | 0 |  | 0 | 0 | -0.0025898 | 0 |  | 0 | 0 | -0.00277 | 0 |  | 0 | 0 | -0.0029257 | 0 |  | 0 | 0 | -0.0030618 | 0 |  | 0 | 0 | -0.0031815 | 0 |  | 0 | 0 | -0.0032878 | 0 |  | 0 | 0 | -0.0033828 | 0 |  | 0 | 0 | -0.0034681 | 0 |  | 0 | 0 | -0.0035452 | 0 |  | 0 | 0 | -0.0036152 | 0 |  | 0 | 0 | -0.0036791 | 0 |  | 0 | 0 | -0.0037376 | 0 |  | 0 | 0 | -0.0037914 | 0 |  | 0 | 0 | -0.003841 | 0 |  | 0 | 0 | -0.0038869 | 0 |  | 0 | 0
72 |  | Concrete | 40 | 62.525 |  |  | 2.9662 | 36.7806 |  |  | -0.0005593 | 0 |  | 0 | 0 |  | -0.0011405 | 0 |  | 0 | 0 |  | -0.0015891 | 0 |  | 0 | 0 |  | -0.0019457 | 0 |  | 0 | 0 |  | -0.002236 | 0 |  | 0 | 0 | -0.0024769 | 0 |  | 0 | 0 | -0.0026801 | 0 |  | 0 | 0 | -0.0028537 | 0 |  | 0 | 0 | -0.0030038 | 0 |  | 0 | 0 | -0.0031348 | 0 |  | 0 | 0 | -0.0032503 | 0 |  | 0 | 0 | -0.0033527 | 0 |  | 0 | 0 | -0.0034442 | 0 |  | 0 | 0 | -0.0035264 | 0 |  | 0 | 0 | -0.0036007 | 0 |  | 0 | 0 | -0.0036682 | 0 |  | 0 | 0 | -0.0037297 | 0 |  | 0 | 0 | -0.0037861 | 0 |  | 0 | 0 | -0.0038379 | 0 |  | 0 | 0 | -0.0038857 | 0 |  | 0 | 0 | -0.0039299 | 0 |  | 0 | 0
73 |  | Concrete | 41 | 62.525 |  |  | 2.307 | 28.6071 |  |  | -0.00072972 | 0 |  | 0 | 0 |  | -0.001289 | 0 |  | 0 | 0 |  | -0.0017206 | 0 |  | 0 | 0 |  | -0.0020637 | 0 |  | 0 | 0 |  | -0.002343 | 0 |  | 0 | 0 | -0.0025749 | 0 |  | 0 | 0 | -0.0027703 | 0 |  | 0 | 0 | -0.0029374 | 0 |  | 0 | 0 | -0.0030818 | 0 |  | 0 | 0 | -0.0032079 | 0 |  | 0 | 0 | -0.003319 | 0 |  | 0 | 0 | -0.0034175 | 0 |  | 0 | 0 | -0.0035056 | 0 |  | 0 | 0 | -0.0035847 | 0 |  | 0 | 0 | -0.0036562 | 0 |  | 0 | 0 | -0.0037211 | 0 |  | 0 | 0 | -0.0037803 | 0 |  | 0 | 0 | -0.0038346 | 0 |  | 0 | 0 | -0.0038844 | 0 |  | 0 | 0 | -0.0039304 | 0 |  | 0 | 0 | -0.003973 | 0 |  | 0 | 0
74 |  | Concrete | 42 | 62.525 |  |  | 1.6479 | 20.4337 |  |  | -0.00090014 | 0 |  | 0 | 0 |  | -0.0014375 | 0 |  | 0 | 0 |  | -0.0018521 | 0 |  | 0 | 0 |  | -0.0021817 | 0 |  | 0 | 0 |  | -0.0024501 | 0 |  | 0 | 0 | -0.0026728 | 0 |  | 0 | 0 | -0.0028606 | 0 |  | 0 | 0 | -0.0030211 | 0 |  | 0 | 0 | -0.0031599 | 0 |  | 0 | 0 | -0.003281 | 0 |  | 0 | 0 | -0.0033877 | 0 |  | 0 | 0 | -0.0034824 | 0 |  | 0 | 0 | -0.003567 | 0 |  | 0 | 0 | -0.003643 | 0 |  | 0 | 0 | -0.0037117 | 0 |  | 0 | 0 | -0.0037741 | 0 |  | 0 | 0 | -0.0038309 | 0 |  | 0 | 0 | -0.0038831 | 0 |  | 0 | 0 | -0.003931 | 0 |  | 0 | 0 | -0.0039751 | 0 |  | 0 | 0 | -0.004016 | 0 |  | 0 | 0
75 |  | Concrete | 43 | 62.525 |  |  | 0.98873 | 12.2602 |  |  | -0.0010706 | 0 |  | 0 | 0 |  | -0.0015859 | 0 |  | 0 | 0 |  | -0.0019836 | 0 |  | 0 | 0 |  | -0.0022997 | 0 |  | 0 | 0 |  | -0.0025571 | 0 |  | 0 | 0 | -0.0027708 | 0 |  | 0 | 0 | -0.0029509 | 0 |  | 0 | 0 | -0.0031048 | 0 |  | 0 | 0 | -0.0032379 | 0 |  | 0 | 0 | -0.0033541 | 0 |  | 0 | 0 | -0.0034564 | 0 |  | 0 | 0 | -0.0035472 | 0 |  | 0 | 0 | -0.0036284 | 0 |  | 0 | 0 | -0.0037013 | 0 |  | 0 | 0 | -0.0037672 | 0 |  | 0 | 0 | -0.003827 | 0 |  | 0 | 0 | -0.0038816 | 0 |  | 0 | 0 | -0.0039315 | 0 |  | 0 | 0 | -0.0039775 | 0 |  | 0 | 0 | -0.0040199 | 0 |  | 0 | 0 | -0.0040591 | 0 |  | 0 | 0
76 |  | Concrete | 44 | 62.525 |  |  | 0.32958 | 4.0867 |  |  | -0.001241 | 0 |  | 0 | 0 |  | -0.0017344 | 0 |  | 0 | 0 |  | -0.0021151 | 0 |  | 0 | 0 |  | -0.0024178 | 0 |  | 0 | 0 |  | -0.0026642 | 0 |  | 0 | 0 | -0.0028687 | 0 |  | 0 | 0 | -0.0030412 | 0 |  | 0 | 0 | -0.0031885 | 0 |  | 0 | 0 | -0.003316 | 0 |  | 0 | 0 | -0.0034272 | 0 |  | 0 | 0 | -0.0035252 | 0 |  | 0 | 0 | -0.0036121 | 0 |  | 0 | 0 | -0.0036898 | 0 |  | 0 | 0 | -0.0037596 | 0 |  | 0 | 0 | -0.0038226 | 0 |  | 0 | 0 | -0.0038799 | 0 |  | 0 | 0 | -0.0039322 | 0 |  | 0 | 0 | -0.00398 | 0 |  | 0 | 0 | -0.004024 | 0 |  | 0 | 0 | -0.0040646 | 0 |  | 0 | 0 | -0.0041021 | 0 |  | 0 | 0
77 |  | Concrete | 45 | 62.525 |  |  | -0.32958 | -4.0867 |  |  | -0.0014114 | 0 |  | 0 | 0 |  | -0.0018828 | 0 |  | 0 | 0 |  | -0.0022466 | 0 |  | 0 | 0 |  | -0.0025358 | 0 |  | 0 | 0 |  | -0.0027713 | 0 |  | 0 | 0 | -0.0029667 | 0 |  | 0 | 0 | -0.0031314 | 0 |  | 0 | 0 | -0.0032723 | 0 |  | 0 | 0 | -0.003394 | 0 |  | 0 | 0 | -0.0035003 | 0 |  | 0 | 0 | -0.0035939 | 0 |  | 0 | 0 | -0.003677 | 0 |  | 0 | 0 | -0.0037512 | 0 |  | 0 | 0 | -0.0038179 | 0 |  | 0 | 0 | -0.0038781 | 0 |  | 0 | 0 | -0.0039329 | 0 |  | 0 | 0 | -0.0039828 | 0 |  | 0 | 0 | -0.0040285 | 0 |  | 0 | 0 | -0.0040705 | 0 |  | 0 | 0 | -0.0041093 | 0 |  | 0 | 0 | -0.0041451 | 0 |  | 0 | 0
78 |  | Concrete | 46 | 62.525 |  |  | -0.98873 | -12.2602 |  |  | -0.0015818 | 0 |  | 0 | 0 |  | -0.0020313 | 0 |  | 0 | 0 |  | -0.0023781 | 0 |  | 0 | 0 |  | -0.0026538 | 0 |  | 0 | 0 |  | -0.0028783 | 0 |  | 0 | 0 | -0.0030646 | 0 |  | 0 | 0 | -0.0032217 | 0 |  | 0 | 0 | -0.003356 | 0 |  | 0 | 0 | -0.003472 | 0 |  | 0 | 0 | -0.0035734 | 0 |  | 0 | 0 | -0.0036626 | 0 |  | 0 | 0 | -0.0037418 | 0 |  | 0 | 0 | -0.0038126 | 0 |  | 0 | 0 | -0.0038762 | 0 |  | 0 | 0 | -0.0039336 | 0 |  | 0 | 0 | -0.0039858 | 0 |  | 0 | 0 | -0.0040334 | 0 |  | 0 | 0 | -0.004077 | 0 |  | 0 | 0 | -0.004117 | 0 |  | 0 | 0 | -0.004154 | 0 |  | 0 | 0 | -0.0041882 | 0 |  | 0 | 0
79 |  | Concrete | 47 | 62.525 |  |  | -1.6479 | -20.4337 |  |  | -0.0017522 | 0 |  | 0 | 0 |  | -0.0021797 | 0 |  | 0 | 0 |  | -0.0025096 | 0 |  | 0 | 0 |  | -0.0027719 | 0 |  | 0 | 0 |  | -0.0029854 | 0 |  | 0 | 0 | -0.0031626 | 0 |  | 0 | 0 | -0.003312 | 0 |  | 0 | 0 | -0.0034397 | 0 |  | 0 | 0 | -0.0035501 | 0 |  | 0 | 0 | -0.0036465 | 0 |  | 0 | 0 | -0.0037314 | 0 |  | 0 | 0 | -0.0038067 | 0 |  | 0 | 0 | -0.003874 | 0 |  | 0 | 0 | -0.0039344 | 0 |  | 0 | 0 | -0.0039891 | 0 |  | 0 | 0 | -0.0040387 | 0 |  | 0 | 0 | -0.004084 | 0 |  | 0 | 0 | -0.0041255 | 0 |  | 0 | 0 | -0.0041636 | 0 |  | 0 | 0 | -0.0041987 | 0 |  | 0 | 0 | -0.0042312 | 0 |  | 0 | 0
80 |  | Concrete | 48 | 62.525 |  |  | -2.307 | -28.6071 |  |  | -0.0019226 | 0 |  | 0 | 0 |  | -0.0023282 | 0 |  | 0 | 0 |  | -0.0026411 | 0 |  | 0 | 0 |  | -0.0028899 | 0 |  | 0 | 0 |  | -0.0030924 | 0 |  | 0 | 0 | -0.0032605 | 0 |  | 0 | 0 | -0.0034023 | 0 |  | 0 | 0 | -0.0035234 | 0 |  | 0 | 0 | -0.0036281 | 0 |  | 0 | 0 | -0.0037196 | 0 |  | 0 | 0 | -0.0038001 | 0 |  | 0 | 0 | -0.0038715 | 0 |  | 0 | 0 | -0.0039354 | 0 |  | 0 | 0 | -0.0039927 | 0 |  | 0 | 0 | -0.0040446 | 0 |  | 0 | 0 | -0.0040917 | 0 |  | 0 | 0 | -0.0041346 | 0 |  | 0 | 0 | -0.0041739 | 0 |  | 0 | 0 | -0.0042101 | 0 |  | 0 | 0 | -0.0042434 | 0 |  | 0 | 0 | -0.0042743 | 0 |  | 0 | 0
81 |  | Concrete | 49 | 62.525 |  |  | -2.9662 | -36.7806 |  |  | -0.0020931 | 0 |  | 0 | 0 |  | -0.0024766 | 0 |  | 0 | 0 |  | -0.0027726 | 0 |  | 0 | 0 |  | -0.0030079 | 0 |  | 0 | 0 |  | -0.0031995 | 0 |  | 0 | 0 | -0.0033585 | 0 |  | 0 | 0 | -0.0034925 | 0 |  | 0 | 0 | -0.0036071 | 0 |  | 0 | 0 | -0.0037062 | 0 |  | 0 | 0 | -0.0037927 | 0 |  | 0 | 0 | -0.0038688 | 0 |  | 0 | 0 | -0.0039364 | 0 |  | 0 | 0 | -0.0039968 | 0 |  | 0 | 0 | -0.004051 | 0 |  | 0 | 0 | -0.0041001 | 0 |  | 0 | 0 | -0.0041446 | 0 |  | 0 | 0 | -0.0041852 | 0 |  | 0 | 0 | -0.0042224 | 0 |  | 0 | 0 | -0.0042566 | 0 |  | 0 | 0 | -0.0042881 | 0 |  | 0 | 0 | -0.0043173 | 0 |  | 0 | 0
82 |  | Concrete | 50 | 62.525 |  |  | -3.6253 | -44.9541 |  |  | -0.0022635 | 0 |  | 0 | 0 |  | -0.0026251 | 0 |  | 0 | 0 |  | -0.0029041 | 0 |  | 0 | 0 |  | -0.0031259 | 0 |  | 0 | 0 |  | -0.0033066 | 0 |  | 0 | 0 | -0.0034564 | 0 |  | 0 | 0 | -0.0035828 | 0 |  | 0 | 0 | -0.0036908 | 0 |  | 0 | 0 | -0.0037842 | 0 |  | 0 | 0 | -0.0038657 | 0 |  | 0 | 0 | -0.0039375 | 0 |  | 0 | 0 | -0.0040012 | 0 |  | 0 | 0 | -0.0040582 | 0 |  | 0 | 0 | -0.0041093 | 0 |  | 0 | 0 | -0.0041556 | 0 |  | 0 | 0 | -0.0041975 | 0 |  | 0 | 0 | -0.0042358 | 0 |  | 0 | 0 | -0.0042709 | 0 |  | 0 | 0 | -0.0043031 | 0 |  | 0 | 0 | -0.0043329 | 0 |  | 0 | 0 | -0.0043604 | 0 |  | 0 | 0
83 |  | Concrete | 51 | 62.525 |  |  | -4.2845 | -53.1275 |  |  | -0.0024339 | 0 |  | 0 | 0 |  | -0.0027735 | 0 |  | 0 | 0 |  | -0.0030356 | 0 |  | 0 | 0 |  | -0.003244 | 0 |  | 0 | 0 |  | -0.0034136 | 0 |  | 0 | 0 | -0.0035544 | 0 |  | 0 | 0 | -0.0036731 | 0 |  | 0 | 0 | -0.0037746 | 0 |  | 0 | 0 | -0.0038623 | 0 |  | 0 | 0 | -0.0039388 | 0 |  | 0 | 0 | -0.0040063 | 0 |  | 0 | 0 | -0.0040661 | 0 |  | 0 | 0 | -0.0041196 | 0 |  | 0 | 0 | -0.0041676 | 0 |  | 0 | 0 | -0.004211 | 0 |  | 0 | 0 | -0.0042505 | 0 |  | 0 | 0 | -0.0042864 | 0 |  | 0 | 0 | -0.0043194 | 0 |  | 0 | 0 | -0.0043496 | 0 |  | 0 | 0 | -0.0043776 | 0 |  | 0 | 0 | -0.0044034 | 0 |  | 0 | 0
84 |  | Concrete | 52 | 62.525 |  |  | -4.9436 | -61.301 |  |  | -0.0026043 | 0 |  | 0 | 0 |  | -0.002922 | 0 |  | 0 | 0 |  | -0.0031671 | 0 |  | 0 | 0 |  | -0.003362 | 0 |  | 0 | 0 |  | -0.0035207 | 0 |  | 0 | 0 | -0.0036523 | 0 |  | 0 | 0 | -0.0037634 | 0 |  | 0 | 0 | -0.0038583 | 0 |  | 0 | 0 | -0.0039403 | 0 |  | 0 | 0 | -0.0040119 | 0 |  | 0 | 0 | -0.004075 | 0 |  | 0 | 0 | -0.004131 | 0 |  | 0 | 0 | -0.004181 | 0 |  | 0 | 0 | -0.0042259 | 0 |  | 0 | 0 | -0.0042665 | 0 |  | 0 | 0 | -0.0043034 | 0 |  | 0 | 0 | -0.004337 | 0 |  | 0 | 0 | -0.0043678 | 0 |  | 0 | 0 | -0.0043962 | 0 |  | 0 | 0 | -0.0044223 | 0 |  | 0 | 0 | -0.0044465 | 0 |  | 0 | 0
85 |  | Concrete | 53 | 62.525 |  |  | -5.6028 | -69.4744 |  |  | -0.0027747 | 0 |  | 0 | 0 |  | -0.0030704 | 0 |  | 0 | 0 |  | -0.0032986 | 0 |  | 0 | 0 |  | -0.00348 | 0 |  | 0 | 0 |  | -0.0036277 | 0 |  | 0 | 0 | -0.0037503 | 0 |  | 0 | 0 | -0.0038536 | 0 |  | 0 | 0 | -0.003942 | 0 |  | 0 | 0 | -0.0040183 | 0 |  | 0 | 0 | -0.004085 | 0 |  | 0 | 0 | -0.0041437 | 0 |  | 0 | 0 | -0.0041958 | 0 |  | 0 | 0 | -0.0042424 | 0 |  | 0 | 0 | -0.0042842 | 0 |  | 0 | 0 | -0.004322 | 0 |  | 0 | 0 | -0.0043563 | 0 |  | 0 | 0 | -0.0043877 | 0 |  | 0 | 0 | -0.0044163 | 0 |  | 0 | 0 | -0.0044427 | 0 |  | 0 | 0 | -0.004467 | 0 |  | 0 | 0 | -0.0044895 | 0 |  | 0 | 0
86 |  | Concrete | 54 | 62.525 |  |  | -6.2619 | -77.6479 |  |  | -0.0029452 | 0 |  | 0 | 0 |  | -0.0032189 | 0 |  | 0 | 0 |  | -0.0034301 | 0 |  | 0 | 0 |  | -0.0035981 | 0 |  | 0 | 0 |  | -0.0037348 | 0 |  | 0 | 0 | -0.0038482 | 0 |  | 0 | 0 | -0.0039439 | 0 |  | 0 | 0 | -0.0040257 | 0 |  | 0 | 0 | -0.0040964 | 0 |  | 0 | 0 | -0.0041581 | 0 |  | 0 | 0 | -0.0042125 | 0 |  | 0 | 0 | -0.0042607 | 0 |  | 0 | 0 | -0.0043038 | 0 |  | 0 | 0 | -0.0043425 | 0 |  | 0 | 0 | -0.0043775 | 0 |  | 0 | 0 | -0.0044093 | 0 |  | 0 | 0 | -0.0044383 | 0 |  | 0 | 0 | -0.0044648 | 0 |  | 0 | 0 | -0.0044892 | 0 |  | 0 | 0 | -0.0045117 | 0 |  | 0 | 0 | -0.0045325 | 0 |  | 0 | 0
87 |  | Concrete | 55 | 62.525 |  |  | -6.9211 | -85.8214 |  |  | -0.0031156 | 0 |  | 0 | 0 |  | -0.0033674 | 0 |  | 0 | 0 |  | -0.0035616 | 0 |  | 0 | 0 |  | -0.0037161 | 0 |  | 0 | 0 |  | -0.0038418 | 0 |  | 0 | 0 | -0.0039462 | 0 |  | 0 | 0 | -0.0040342 | 0 |  | 0 | 0 | -0.0041094 | 0 |  | 0 | 0 | -0.0041744 | 0 |  | 0 | 0 | -0.0042312 | 0 |  | 0 | 0 | -0.0042812 | 0 |  | 0 | 0 | -0.0043255 | 0 |  | 0 | 0 | -0.0043652 | 0 |  | 0 | 0 | -0.0044008 | 0 |  | 0 | 0 | -0.004433 | 0 |  | 0 | 0 | -0.0044622 | 0 |  | 0 | 0 | -0.0044889 | 0 |  | 0 | 0 | -0.0045133 | 0 |  | 0 | 0 | -0.0045357 | 0 |  | 0 | 0 | -0.0045564 | 0 |  | 0 | 0 | -0.0045756 | 0 |  | 0 | 0
88 |  | Concrete | 56 | 62.525 |  |  | -7.5802 | -93.9948 |  |  | -0.003286 | 0 |  | 0 | 0 |  | -0.0035158 | 0 |  | 0 | 0 |  | -0.0036931 | 0 |  | 0 | 0 |  | -0.0038341 | 0 |  | 0 | 0 |  | -0.0039489 | 0 |  | 0 | 0 | -0.0040442 | 0 |  | 0 | 0 | -0.0041245 | 0 |  | 0 | 0 | -0.0041931 | 0 |  | 0 | 0 | -0.0042525 | 0 |  | 0 | 0 | -0.0043043 | 0 |  | 0 | 0 | -0.0043499 | 0 |  | 0 | 0 | -0.0043904 | 0 |  | 0 | 0 | -0.0044266 | 0 |  | 0 | 0 | -0.0044591 | 0 |  | 0 | 0 | -0.0044885 | 0 |  | 0 | 0 | -0.0045151 | 0 |  | 0 | 0 | -0.0045395 | 0 |  | 0 | 0 | -0.0045618 | 0 |  | 0 | 0 | -0.0045823 | 0 |  | 0 | 0 | -0.0046011 | 0 |  | 0 | 0 | -0.0046186 | 0 |  | 0 | 0
89 |  | Concrete | 57 | 62.525 |  |  | -8.2394 | -102.1683 |  |  | -0.0034564 | 0 |  | 0 | 0 |  | -0.0036643 | 0 |  | 0 | 0 |  | -0.0038246 | 0 |  | 0 | 0 |  | -0.0039522 | 0 |  | 0 | 0 |  | -0.004056 | 0 |  | 0 | 0 | -0.0041421 | 0 |  | 0 | 0 | -0.0042148 | 0 |  | 0 | 0 | -0.0042768 | 0 |  | 0 | 0 | -0.0043305 | 0 |  | 0 | 0 | -0.0043774 | 0 |  | 0 | 0 | -0.0044186 | 0 |  | 0 | 0 | -0.0044553 | 0 |  | 0 | 0 | -0.004488 | 0 |  | 0 | 0 | -0.0045174 | 0 |  | 0 | 0 | -0.004544 | 0 |  | 0 | 0 | -0.0045681 | 0 |  | 0 | 0 | -0.0045901 | 0 |  | 0 | 0 | -0.0046102 | 0 |  | 0 | 0 | -0.0046288 | 0 |  | 0 | 0 | -0.0046459 | 0 |  | 0 | 0 | -0.0046617 | 0 |  | 0 | 0
90 |  | Concrete | 58 | 62.525 |  |  | -8.8985 | -110.3418 |  |  | -0.0036268 | 0 |  | 0 | 0 |  | -0.0038127 | 0 |  | 0 | 0 |  | -0.0039561 | 0 |  | 0 | 0 |  | -0.0040702 | 0 |  | 0 | 0 |  | -0.004163 | 0 |  | 0 | 0 | -0.0042401 | 0 |  | 0 | 0 | -0.004305 | 0 |  | 0 | 0 | -0.0043606 | 0 |  | 0 | 0 | -0.0044086 | 0 |  | 0 | 0 | -0.0044505 | 0 |  | 0 | 0 | -0.0044874 | 0 |  | 0 | 0 | -0.0045201 | 0 |  | 0 | 0 | -0.0045494 | 0 |  | 0 | 0 | -0.0045757 | 0 |  | 0 | 0 | -0.0045994 | 0 |  | 0 | 0 | -0.004621 | 0 |  | 0 | 0 | -0.0046407 | 0 |  | 0 | 0 | -0.0046587 | 0 |  | 0 | 0 | -0.0046753 | 0 |  | 0 | 0 | -0.0046906 | 0 |  | 0 | 0 | -0.0047047 | 0 |  | 0 | 0
91 |  | Concrete | 59 | 62.525 |  |  | -9.5577 | -118.5152 |  |  | -0.0037973 | 0 |  | 0 | 0 |  | -0.0039612 | 0 |  | 0 | 0 |  | -0.0040876 | 0 |  | 0 | 0 |  | -0.0041882 | 0 |  | 0 | 0 |  | -0.0042701 | 0 |  | 0 | 0 | -0.004338 | 0 |  | 0 | 0 | -0.0043953 | 0 |  | 0 | 0 | -0.0044443 | 0 |  | 0 | 0 | -0.0044866 | 0 |  | 0 | 0 | -0.0045236 | 0 |  | 0 | 0 | -0.0045561 | 0 |  | 0 | 0 | -0.004585 | 0 |  | 0 | 0 | -0.0046108 | 0 |  | 0 | 0 | -0.004634 | 0 |  | 0 | 0 | -0.0046549 | 0 |  | 0 | 0 | -0.004674 | 0 |  | 0 | 0 | -0.0046913 | 0 |  | 0 | 0 | -0.0047072 | 0 |  | 0 | 0 | -0.0047218 | 0 |  | 0 | 0 | -0.0047353 | 0 |  | 0 | 0 | -0.0047478 | 0 |  | 0 | 0
92 |  | Concrete | 60 | 62.525 |  |  | -10.2168 | -126.6887 |  |  | -0.0039677 | 0 |  | 0 | 0 |  | -0.0041096 | 0 |  | 0 | 0 |  | -0.0042192 | 0 |  | 0 | 0 |  | -0.0043062 | 0 |  | 0 | 0 |  | -0.0043771 | 0 |  | 0 | 0 | -0.004436 | 0 |  | 0 | 0 | -0.0044856 | 0 |  | 0 | 0 | -0.004528 | 0 |  | 0 | 0 | -0.0045646 | 0 |  | 0 | 0 | -0.0045966 | 0 |  | 0 | 0 | -0.0046248 | 0 |  | 0 | 0 | -0.0046498 | 0 |  | 0 | 0 | -0.0046722 | 0 |  | 0 | 0 | -0.0046923 | 0 |  | 0 | 0 | -0.0047104 | 0 |  | 0 | 0 | -0.0047269 | 0 |  | 0 | 0 | -0.0047419 | 0 |  | 0 | 0 | -0.0047557 | 0 |  | 0 | 0 | -0.0047683 | 0 |  | 0 | 0 | -0.00478 | 0 |  | 0 | 0 | -0.0047908 | 0 |  | 0 | 0
93 |  | Concrete | 61 | 62.525 |  |  | -10.876 | -134.8622 |  |  | -0.0041381 | 0 |  | 0 | 0 |  | -0.0042581 | 0 |  | 0 | 0 |  | -0.0043507 | 0 |  | 0 | 0 |  | -0.0044243 | 0 |  | 0 | 0 |  | -0.0044842 | 0 |  | 0 | 0 | -0.0045339 | 0 |  | 0 | 0 | -0.0045759 | 0 |  | 0 | 0 | -0.0046117 | 0 |  | 0 | 0 | -0.0046427 | 0 |  | 0 | 0 | -0.0046697 | 0 |  | 0 | 0 | -0.0046936 | 0 |  | 0 | 0 | -0.0047147 | 0 |  | 0 | 0 | -0.0047336 | 0 |  | 0 | 0 | -0.0047506 | 0 |  | 0 | 0 | -0.0047659 | 0 |  | 0 | 0 | -0.0047798 | 0 |  | 0 | 0 | -0.0047925 | 0 |  | 0 | 0 | -0.0048042 | 0 |  | 0 | 0 | -0.0048149 | 0 |  | 0 | 0 | -0.0048247 | 0 |  | 0 | 0 | -0.0048338 | 0 |  | 0 | 0
94 |  | Concrete | 62 | 62.525 |  |  | -11.5351 | -143.0356 |  |  | -0.0043085 | 0 |  | 0 | 0 |  | -0.0044065 | 0 |  | 0 | 0 |  | -0.0044822 | 0 |  | 0 | 0 |  | -0.0045423 | 0 |  | 0 | 0 |  | -0.0045912 | 0 |  | 0 | 0 | -0.0046319 | 0 |  | 0 | 0 | -0.0046661 | 0 |  | 0 | 0 | -0.0046954 | 0 |  | 0 | 0 | -0.0047207 | 0 |  | 0 | 0 | -0.0047428 | 0 |  | 0 | 0 | -0.0047623 | 0 |  | 0 | 0 | -0.0047796 | 0 |  | 0 | 0 | -0.004795 | 0 |  | 0 | 0 | -0.0048088 | 0 |  | 0 | 0 | -0.0048214 | 0 |  | 0 | 0 | -0.0048328 | 0 |  | 0 | 0 | -0.0048431 | 0 |  | 0 | 0 | -0.0048526 | 0 |  | 0 | 0 | -0.0048614 | 0 |  | 0 | 0 | -0.0048694 | 0 |  | 0 | 0 | -0.0048769 | 0 |  | 0 | 0
95 |  | Concrete | 63 | 62.525 |  |  | -12.1943 | -151.2091 |  |  | -0.0044789 | 0 |  | 0 | 0 |  | -0.004555 | 0 |  | 0 | 0 |  | -0.0046137 | 0 |  | 0 | 0 |  | -0.0046603 | 0 |  | 0 | 0 |  | -0.0046983 | 0 |  | 0 | 0 | -0.0047298 | 0 |  | 0 | 0 | -0.0047564 | 0 |  | 0 | 0 | -0.0047791 | 0 |  | 0 | 0 | -0.0047988 | 0 |  | 0 | 0 | -0.0048159 | 0 |  | 0 | 0 | -0.004831 | 0 |  | 0 | 0 | -0.0048444 | 0 |  | 0 | 0 | -0.0048564 | 0 |  | 0 | 0 | -0.0048671 | 0 |  | 0 | 0 | -0.0048769 | 0 |  | 0 | 0 | -0.0048857 | 0 |  | 0 | 0 | -0.0048937 | 0 |  | 0 | 0 | -0.0049011 | 0 |  | 0 | 0 | -0.0049079 | 0 |  | 0 | 0 | -0.0049142 | 0 |  | 0 | 0 | -0.0049199 | 0 |  | 0 | 0
96 |  | Concrete | 64 | 62.525 |  |  | -12.8534 | -159.3826 |  |  | -0.0046494 | 0 |  | 0 | 0 |  | -0.0047034 | 0 |  | 0 | 0 |  | -0.0047452 | 0 |  | 0 | 0 |  | -0.0047784 | 0 |  | 0 | 0 |  | -0.0048054 | 0 |  | 0 | 0 | -0.0048278 | 0 |  | 0 | 0 | -0.0048467 | 0 |  | 0 | 0 | -0.0048628 | 0 |  | 0 | 0 | -0.0048768 | 0 |  | 0 | 0 | -0.004889 | 0 |  | 0 | 0 | -0.0048997 | 0 |  | 0 | 0 | -0.0049093 | 0 |  | 0 | 0 | -0.0049178 | 0 |  | 0 | 0 | -0.0049254 | 0 |  | 0 | 0 | -0.0049323 | 0 |  | 0 | 0 | -0.0049386 | 0 |  | 0 | 0 | -0.0049444 | 0 |  | 0 | 0 | -0.0049496 | 0 |  | 0 | 0 | -0.0049544 | 0 |  | 0 | 0 | -0.0049589 | 0 |  | 0 | 0 | -0.004963 | 0 |  | 0 | 0
97 |  | Concrete | 65 | 32 |  |  | -13.3438 | -165.4628 |  |  | -0.0047761 | 0 |  | 0 | 0 |  | -0.0048139 | 0 |  | 0 | 0 |  | -0.004843 | 0 |  | 0 | 0 |  | -0.0048662 | 0 |  | 0 | 0 |  | -0.004885 | 0 |  | 0 | 0 | -0.0049006 | 0 |  | 0 | 0 | -0.0049138 | 0 |  | 0 | 0 | -0.0049251 | 0 |  | 0 | 0 | -0.0049349 | 0 |  | 0 | 0 | -0.0049434 | 0 |  | 0 | 0 | -0.0049509 | 0 |  | 0 | 0 | -0.0049575 | 0 |  | 0 | 0 | -0.0049635 | 0 |  | 0 | 0 | -0.0049688 | 0 |  | 0 | 0 | -0.0049736 | 0 |  | 0 | 0 | -0.004978 | 0 |  | 0 | 0 | -0.004982 | 0 |  | 0 | 0 | -0.0049857 | 0 |  | 0 | 0 | -0.004989 | 0 |  | 0 | 0 | -0.0049921 | 0 |  | 0 | 0 | -0.004995 | 0 |  | 0 | 0
98 |  | Concrete | 66 | 32 |  |  | -13.6653 | -169.4499 |  |  | -0.0048593 | 0 |  | 0 | 0 |  | -0.0048863 | 0 |  | 0 | 0 |  | -0.0049071 | 0 |  | 0 | 0 |  | -0.0049237 | 0 |  | 0 | 0 |  | -0.0049372 | 0 |  | 0 | 0 | -0.0049484 | 0 |  | 0 | 0 | -0.0049579 | 0 |  | 0 | 0 | -0.004966 | 0 |  | 0 | 0 | -0.0049729 | 0 |  | 0 | 0 | -0.004979 | 0 |  | 0 | 0 | -0.0049844 | 0 |  | 0 | 0 | -0.0049892 | 0 |  | 0 | 0 | -0.0049934 | 0 |  | 0 | 0 | -0.0049972 | 0 |  | 0 | 0 | -0.0050007 | 0 |  | 0 | 0 | -0.0050038 | 0 |  | 0 | 0 | -0.0050067 | 0 |  | 0 | 0 | -0.0050093 | 0 |  | 0 | 0 | -0.0050117 | 0 |  | 0 | 0 | -0.0050139 | 0 |  | 0 | 0 | -0.005016 | 0 |  | 0 | 0
99 |  | Concrete | 67 | 32 |  |  | -13.9868 | -173.4369 |  |  | -0.0049424 | 0 |  | 0 | 0 |  | -0.0049587 | 0 |  | 0 | 0 |  | -0.0049713 | 0 |  | 0 | 0 |  | -0.0049813 | 0 |  | 0 | 0 |  | -0.0049895 | 0 |  | 0 | 0 | -0.0049962 | 0 |  | 0 | 0 | -0.0050019 | 0 |  | 0 | 0 | -0.0050068 | 0 |  | 0 | 0 | -0.005011 | 0 |  | 0 | 0 | -0.0050147 | 0 |  | 0 | 0 | -0.0050179 | 0 |  | 0 | 0 | -0.0050208 | 0 |  | 0 | 0 | -0.0050234 | 0 |  | 0 | 0 | -0.0050257 | 0 |  | 0 | 0 | -0.0050278 | 0 |  | 0 | 0 | -0.0050296 | 0 |  | 0 | 0 | -0.0050314 | 0 |  | 0 | 0 | -0.005033 | 0 |  | 0 | 0 | -0.0050344 | 0 |  | 0 | 0 | -0.0050358 | 0 |  | 0 | 0 | -0.005037 | 0 |  | 0 | 0
100 |  | Concrete | 68 | 32 |  |  | -14.3084 | -177.424 |  |  | -0.0050255 | 0 |  | 0 | 0 |  | -0.0050311 | 0 |  | 0 | 0 |  | -0.0050354 | 0 |  | 0 | 0 |  | -0.0050389 | 0 |  | 0 | 0 |  | -0.0050417 | 0 |  | 0 | 0 | -0.005044 | 0 |  | 0 | 0 | -0.005046 | 0 |  | 0 | 0 | -0.0050476 | 0 |  | 0 | 0 | -0.0050491 | 0 |  | 0 | 0 | -0.0050503 | 0 |  | 0 | 0 | -0.0050514 | 0 |  | 0 | 0 | -0.0050524 | 0 |  | 0 | 0 | -0.0050533 | 0 |  | 0 | 0 | -0.0050541 | 0 |  | 0 | 0 | -0.0050548 | 0 |  | 0 | 0 | -0.0050555 | 0 |  | 0 | 0 | -0.0050561 | 0 |  | 0 | 0 | -0.0050566 | 0 |  | 0 | 0 | -0.0050571 | 0 |  | 0 | 0 | -0.0050576 | 0 |  | 0 | 0 | -0.005058 | 0 |  | 0 | 0
101 |  | Concrete | 69 | 27.45 |  |  | -52.224 | -172.3598 |  |  | -0.0049199 | 0 |  | 0 | 0 |  | -0.0049391 | 0 |  | 0 | 0 |  | -0.004954 | 0 |  | 0 | 0 |  | -0.0049657 | 0 |  | 0 | 0 |  | -0.0049753 | 0 |  | 0 | 0 | -0.0049833 | 0 |  | 0 | 0 | -0.00499 | 0 |  | 0 | 0 | -0.0049958 | 0 |  | 0 | 0 | -0.0050007 | 0 |  | 0 | 0 | -0.005005 | 0 |  | 0 | 0 | -0.0050089 | 0 |  | 0 | 0 | -0.0050122 | 0 |  | 0 | 0 | -0.0050153 | 0 |  | 0 | 0 | -0.005018 | 0 |  | 0 | 0 | -0.0050204 | 0 |  | 0 | 0 | -0.0050227 | 0 |  | 0 | 0 | -0.0050247 | 0 |  | 0 | 0 | -0.0050266 | 0 |  | 0 | 0 | -0.0050283 | 0 |  | 0 | 0 | -0.0050299 | 0 |  | 0 | 0 | -0.0050313 | 0 |  | 0 | 0
102 |  | Concrete | 70 | 27.45 |  |  | -48.6357 | -172.6492 |  |  | -0.004926 | 0 |  | 0 | 0 |  | -0.0049444 | 0 |  | 0 | 0 |  | -0.0049586 | 0 |  | 0 | 0 |  | -0.0049699 | 0 |  | 0 | 0 |  | -0.0049791 | 0 |  | 0 | 0 | -0.0049868 | 0 |  | 0 | 0 | -0.0049932 | 0 |  | 0 | 0 | -0.0049987 | 0 |  | 0 | 0 | -0.0050035 | 0 |  | 0 | 0 | -0.0050076 | 0 |  | 0 | 0 | -0.0050113 | 0 |  | 0 | 0 | -0.0050145 | 0 |  | 0 | 0 | -0.0050174 | 0 |  | 0 | 0 | -0.0050201 | 0 |  | 0 | 0 | -0.0050224 | 0 |  | 0 | 0 | -0.0050245 | 0 |  | 0 | 0 | -0.0050265 | 0 |  | 0 | 0 | -0.0050283 | 0 |  | 0 | 0 | -0.0050299 | 0 |  | 0 | 0 | -0.0050314 | 0 |  | 0 | 0 | -0.0050328 | 0 |  | 0 | 0
103 |  | Concrete | 71 | 27.45 |  |  | -45.0473 | -172.9385 |  |  | -0.004932 | 0 |  | 0 | 0 |  | -0.0049497 | 0 |  | 0 | 0 |  | -0.0049633 | 0 |  | 0 | 0 |  | -0.0049741 | 0 |  | 0 | 0 |  | -0.0049829 | 0 |  | 0 | 0 | -0.0049902 | 0 |  | 0 | 0 | -0.0049964 | 0 |  | 0 | 0 | -0.0050017 | 0 |  | 0 | 0 | -0.0050062 | 0 |  | 0 | 0 | -0.0050102 | 0 |  | 0 | 0 | -0.0050137 | 0 |  | 0 | 0 | -0.0050168 | 0 |  | 0 | 0 | -0.0050196 | 0 |  | 0 | 0 | -0.0050221 | 0 |  | 0 | 0 | -0.0050244 | 0 |  | 0 | 0 | -0.0050264 | 0 |  | 0 | 0 | -0.0050283 | 0 |  | 0 | 0 | -0.00503 | 0 |  | 0 | 0 | -0.0050316 | 0 |  | 0 | 0 | -0.005033 | 0 |  | 0 | 0 | -0.0050344 | 0 |  | 0 | 0
104 |  | Concrete | 72 | 27.45 |  |  | -41.4589 | -173.2279 |  |  | -0.004938 | 0 |  | 0 | 0 |  | -0.0049549 | 0 |  | 0 | 0 |  | -0.0049679 | 0 |  | 0 | 0 |  | -0.0049783 | 0 |  | 0 | 0 |  | -0.0049867 | 0 |  | 0 | 0 | -0.0049937 | 0 |  | 0 | 0 | -0.0049996 | 0 |  | 0 | 0 | -0.0050046 | 0 |  | 0 | 0 | -0.005009 | 0 |  | 0 | 0 | -0.0050128 | 0 |  | 0 | 0 | -0.0050162 | 0 |  | 0 | 0 | -0.0050191 | 0 |  | 0 | 0 | -0.0050218 | 0 |  | 0 | 0 | -0.0050242 | 0 |  | 0 | 0 | -0.0050263 | 0 |  | 0 | 0 | -0.0050283 | 0 |  | 0 | 0 | -0.0050301 | 0 |  | 0 | 0 | -0.0050317 | 0 |  | 0 | 0 | -0.0050332 | 0 |  | 0 | 0 | -0.0050346 | 0 |  | 0 | 0 | -0.0050359 | 0 |  | 0 | 0
105 |  | Concrete | 73 | 27.45 |  |  | -37.8706 | -173.5173 |  |  | -0.0049441 | 0 |  | 0 | 0 |  | -0.0049602 | 0 |  | 0 | 0 |  | -0.0049726 | 0 |  | 0 | 0 |  | -0.0049825 | 0 |  | 0 | 0 |  | -0.0049905 | 0 |  | 0 | 0 | -0.0049972 | 0 |  | 0 | 0 | -0.0050028 | 0 |  | 0 | 0 | -0.0050076 | 0 |  | 0 | 0 | -0.0050118 | 0 |  | 0 | 0 | -0.0050154 | 0 |  | 0 | 0 | -0.0050186 | 0 |  | 0 | 0 | -0.0050214 | 0 |  | 0 | 0 | -0.005024 | 0 |  | 0 | 0 | -0.0050262 | 0 |  | 0 | 0 | -0.0050283 | 0 |  | 0 | 0 | -0.0050302 | 0 |  | 0 | 0 | -0.0050319 | 0 |  | 0 | 0 | -0.0050334 | 0 |  | 0 | 0 | -0.0050349 | 0 |  | 0 | 0 | -0.0050362 | 0 |  | 0 | 0 | -0.0050374 | 0 |  | 0 | 0
106 |  | Concrete | 74 | 27.45 |  |  | -34.2822 | -173.8067 |  |  | -0.0049501 | 0 |  | 0 | 0 |  | -0.0049654 | 0 |  | 0 | 0 |  | -0.0049772 | 0 |  | 0 | 0 |  | -0.0049866 | 0 |  | 0 | 0 |  | -0.0049943 | 0 |  | 0 | 0 | -0.0050006 | 0 |  | 0 | 0 | -0.005006 | 0 |  | 0 | 0 | -0.0050106 | 0 |  | 0 | 0 | -0.0050145 | 0 |  | 0 | 0 | -0.005018 | 0 |  | 0 | 0 | -0.005021 | 0 |  | 0 | 0 | -0.0050237 | 0 |  | 0 | 0 | -0.0050261 | 0 |  | 0 | 0 | -0.0050283 | 0 |  | 0 | 0 | -0.0050303 | 0 |  | 0 | 0 | -0.005032 | 0 |  | 0 | 0 | -0.0050337 | 0 |  | 0 | 0 | -0.0050352 | 0 |  | 0 | 0 | -0.0050365 | 0 |  | 0 | 0 | -0.0050378 | 0 |  | 0 | 0 | -0.0050389 | 0 |  | 0 | 0
107 |  | Concrete | 75 | 27.45 |  |  | -30.6939 | -174.0961 |  |  | -0.0049561 | 0 |  | 0 | 0 |  | -0.0049707 | 0 |  | 0 | 0 |  | -0.0049819 | 0 |  | 0 | 0 |  | -0.0049908 | 0 |  | 0 | 0 |  | -0.0049981 | 0 |  | 0 | 0 | -0.0050041 | 0 |  | 0 | 0 | -0.0050092 | 0 |  | 0 | 0 | -0.0050135 | 0 |  | 0 | 0 | -0.0050173 | 0 |  | 0 | 0 | -0.0050206 | 0 |  | 0 | 0 | -0.0050235 | 0 |  | 0 | 0 | -0.005026 | 0 |  | 0 | 0 | -0.0050283 | 0 |  | 0 | 0 | -0.0050304 | 0 |  | 0 | 0 | -0.0050322 | 0 |  | 0 | 0 | -0.0050339 | 0 |  | 0 | 0 | -0.0050355 | 0 |  | 0 | 0 | -0.0050369 | 0 |  | 0 | 0 | -0.0050382 | 0 |  | 0 | 0 | -0.0050394 | 0 |  | 0 | 0 | -0.0050405 | 0 |  | 0 | 0
108 |  | Concrete | 76 | 27.45 |  |  | -27.1055 | -174.3855 |  |  | -0.0049622 | 0 |  | 0 | 0 |  | -0.0049759 | 0 |  | 0 | 0 |  | -0.0049866 | 0 |  | 0 | 0 |  | -0.004995 | 0 |  | 0 | 0 |  | -0.0050019 | 0 |  | 0 | 0 | -0.0050076 | 0 |  | 0 | 0 | -0.0050124 | 0 |  | 0 | 0 | -0.0050165 | 0 |  | 0 | 0 | -0.0050201 | 0 |  | 0 | 0 | -0.0050232 | 0 |  | 0 | 0 | -0.0050259 | 0 |  | 0 | 0 | -0.0050283 | 0 |  | 0 | 0 | -0.0050305 | 0 |  | 0 | 0 | -0.0050324 | 0 |  | 0 | 0 | -0.0050342 | 0 |  | 0 | 0 | -0.0050358 | 0 |  | 0 | 0 | -0.0050373 | 0 |  | 0 | 0 | -0.0050386 | 0 |  | 0 | 0 | -0.0050398 | 0 |  | 0 | 0 | -0.0050409 | 0 |  | 0 | 0 | -0.005042 | 0 |  | 0 | 0
109 |  | Concrete | 77 | 27.45 |  |  | -23.5172 | -174.6748 |  |  | -0.0049682 | 0 |  | 0 | 0 |  | -0.0049812 | 0 |  | 0 | 0 |  | -0.0049912 | 0 |  | 0 | 0 |  | -0.0049992 | 0 |  | 0 | 0 |  | -0.0050057 | 0 |  | 0 | 0 | -0.005011 | 0 |  | 0 | 0 | -0.0050156 | 0 |  | 0 | 0 | -0.0050195 | 0 |  | 0 | 0 | -0.0050228 | 0 |  | 0 | 0 | -0.0050258 | 0 |  | 0 | 0 | -0.0050283 | 0 |  | 0 | 0 | -0.0050306 | 0 |  | 0 | 0 | -0.0050327 | 0 |  | 0 | 0 | -0.0050345 | 0 |  | 0 | 0 | -0.0050362 | 0 |  | 0 | 0 | -0.0050377 | 0 |  | 0 | 0 | -0.005039 | 0 |  | 0 | 0 | -0.0050403 | 0 |  | 0 | 0 | -0.0050415 | 0 |  | 0 | 0 | -0.0050425 | 0 |  | 0 | 0 | -0.0050435 | 0 |  | 0 | 0
110 |  | Concrete | 78 | 27.45 |  |  | -19.9288 | -174.9642 |  |  | -0.0049742 | 0 |  | 0 | 0 |  | -0.0049864 | 0 |  | 0 | 0 |  | -0.0049959 | 0 |  | 0 | 0 |  | -0.0050034 | 0 |  | 0 | 0 |  | -0.0050095 | 0 |  | 0 | 0 | -0.0050145 | 0 |  | 0 | 0 | -0.0050188 | 0 |  | 0 | 0 | -0.0050224 | 0 |  | 0 | 0 | -0.0050256 | 0 |  | 0 | 0 | -0.0050283 | 0 |  | 0 | 0 | -0.0050308 | 0 |  | 0 | 0 | -0.0050329 | 0 |  | 0 | 0 | -0.0050348 | 0 |  | 0 | 0 | -0.0050366 | 0 |  | 0 | 0 | -0.0050381 | 0 |  | 0 | 0 | -0.0050395 | 0 |  | 0 | 0 | -0.0050408 | 0 |  | 0 | 0 | -0.005042 | 0 |  | 0 | 0 | -0.0050431 | 0 |  | 0 | 0 | -0.0050441 | 0 |  | 0 | 0 | -0.005045 | 0 |  | 0 | 0
111 |  | Concrete | 79 | 36.6 |  |  | 35.2919 | -179.4175 |  |  | -0.0050671 | 0 |  | 0 | 0 |  | -0.0050673 | 0 |  | 0 | 0 |  | -0.0050675 | 0 |  | 0 | 0 |  | -0.0050677 | 0 |  | 0 | 0 |  | -0.0050678 | 0 |  | 0 | 0 | -0.0050679 | 0 |  | 0 | 0 | -0.005068 | 0 |  | 0 | 0 | -0.005068 | 0 |  | 0 | 0 | -0.0050681 | 0 |  | 0 | 0 | -0.0050682 | 0 |  | 0 | 0 | -0.0050682 | 0 |  | 0 | 0 | -0.0050683 | 0 |  | 0 | 0 | -0.0050683 | 0 |  | 0 | 0 | -0.0050683 | 0 |  | 0 | 0 | -0.0050684 | 0 |  | 0 | 0 | -0.0050684 | 0 |  | 0 | 0 | -0.0050684 | 0 |  | 0 | 0 | -0.0050684 | 0 |  | 0 | 0 | -0.0050685 | 0 |  | 0 | 0 | -0.0050685 | 0 |  | 0 | 0 | -0.0050685 | 0 |  | 0 | 0
112 |  | Concrete | 80 | 36.6 |  |  | 30.5074 | -179.0317 |  |  | -0.005059 | 0 |  | 0 | 0 |  | -0.0050603 | 0 |  | 0 | 0 |  | -0.0050613 | 0 |  | 0 | 0 |  | -0.0050621 | 0 |  | 0 | 0 |  | -0.0050627 | 0 |  | 0 | 0 | -0.0050633 | 0 |  | 0 | 0 | -0.0050637 | 0 |  | 0 | 0 | -0.0050641 | 0 |  | 0 | 0 | -0.0050644 | 0 |  | 0 | 0 | -0.0050647 | 0 |  | 0 | 0 | -0.005065 | 0 |  | 0 | 0 | -0.0050652 | 0 |  | 0 | 0 | -0.0050654 | 0 |  | 0 | 0 | -0.0050656 | 0 |  | 0 | 0 | -0.0050657 | 0 |  | 0 | 0 | -0.0050659 | 0 |  | 0 | 0 | -0.005066 | 0 |  | 0 | 0 | -0.0050661 | 0 |  | 0 | 0 | -0.0050663 | 0 |  | 0 | 0 | -0.0050664 | 0 |  | 0 | 0 | -0.0050665 | 0 |  | 0 | 0
113 |  | Concrete | 81 | 36.6 |  |  | 25.7229 | -178.6458 |  |  | -0.005051 | 0 |  | 0 | 0 |  | -0.0050533 | 0 |  | 0 | 0 |  | -0.0050551 | 0 |  | 0 | 0 |  | -0.0050565 | 0 |  | 0 | 0 |  | -0.0050577 | 0 |  | 0 | 0 | -0.0050586 | 0 |  | 0 | 0 | -0.0050594 | 0 |  | 0 | 0 | -0.0050601 | 0 |  | 0 | 0 | -0.0050607 | 0 |  | 0 | 0 | -0.0050613 | 0 |  | 0 | 0 | -0.0050617 | 0 |  | 0 | 0 | -0.0050621 | 0 |  | 0 | 0 | -0.0050625 | 0 |  | 0 | 0 | -0.0050628 | 0 |  | 0 | 0 | -0.0050631 | 0 |  | 0 | 0 | -0.0050634 | 0 |  | 0 | 0 | -0.0050636 | 0 |  | 0 | 0 | -0.0050639 | 0 |  | 0 | 0 | -0.0050641 | 0 |  | 0 | 0 | -0.0050643 | 0 |  | 0 | 0 | -0.0050644 | 0 |  | 0 | 0
114 |  | Concrete | 82 | 36.6 |  |  | 20.9385 | -178.26 |  |  | -0.005043 | 0 |  | 0 | 0 |  | -0.0050463 | 0 |  | 0 | 0 |  | -0.0050489 | 0 |  | 0 | 0 |  | -0.005051 | 0 |  | 0 | 0 |  | -0.0050526 | 0 |  | 0 | 0 | -0.005054 | 0 |  | 0 | 0 | -0.0050552 | 0 |  | 0 | 0 | -0.0050562 | 0 |  | 0 | 0 | -0.0050571 | 0 |  | 0 | 0 | -0.0050578 | 0 |  | 0 | 0 | -0.0050585 | 0 |  | 0 | 0 | -0.0050591 | 0 |  | 0 | 0 | -0.0050596 | 0 |  | 0 | 0 | -0.0050601 | 0 |  | 0 | 0 | -0.0050605 | 0 |  | 0 | 0 | -0.0050609 | 0 |  | 0 | 0 | -0.0050612 | 0 |  | 0 | 0 | -0.0050616 | 0 |  | 0 | 0 | -0.0050619 | 0 |  | 0 | 0 | -0.0050621 | 0 |  | 0 | 0 | -0.0050624 | 0 |  | 0 | 0
115 |  | Concrete | 83 | 36.6 |  |  | 16.154 | -177.8741 |  |  | -0.0050349 | 0 |  | 0 | 0 |  | -0.0050393 | 0 |  | 0 | 0 |  | -0.0050427 | 0 |  | 0 | 0 |  | -0.0050454 | 0 |  | 0 | 0 |  | -0.0050476 | 0 |  | 0 | 0 | -0.0050494 | 0 |  | 0 | 0 | -0.0050509 | 0 |  | 0 | 0 | -0.0050522 | 0 |  | 0 | 0 | -0.0050534 | 0 |  | 0 | 0 | -0.0050544 | 0 |  | 0 | 0 | -0.0050552 | 0 |  | 0 | 0 | -0.005056 | 0 |  | 0 | 0 | -0.0050567 | 0 |  | 0 | 0 | -0.0050573 | 0 |  | 0 | 0 | -0.0050579 | 0 |  | 0 | 0 | -0.0050584 | 0 |  | 0 | 0 | -0.0050589 | 0 |  | 0 | 0 | -0.0050593 | 0 |  | 0 | 0 | -0.0050597 | 0 |  | 0 | 0 | -0.00506 | 0 |  | 0 | 0 | -0.0050604 | 0 |  | 0 | 0
116 |  | Concrete | 84 | 36.6 |  |  | 11.3695 | -177.4883 |  |  | -0.0050269 | 0 |  | 0 | 0 |  | -0.0050323 | 0 |  | 0 | 0 |  | -0.0050365 | 0 |  | 0 | 0 |  | -0.0050398 | 0 |  | 0 | 0 |  | -0.0050425 | 0 |  | 0 | 0 | -0.0050448 | 0 |  | 0 | 0 | -0.0050467 | 0 |  | 0 | 0 | -0.0050483 | 0 |  | 0 | 0 | -0.0050497 | 0 |  | 0 | 0 | -0.0050509 | 0 |  | 0 | 0 | -0.005052 | 0 |  | 0 | 0 | -0.0050529 | 0 |  | 0 | 0 | -0.0050538 | 0 |  | 0 | 0 | -0.0050546 | 0 |  | 0 | 0 | -0.0050553 | 0 |  | 0 | 0 | -0.0050559 | 0 |  | 0 | 0 | -0.0050565 | 0 |  | 0 | 0 | -0.005057 | 0 |  | 0 | 0 | -0.0050575 | 0 |  | 0 | 0 | -0.0050579 | 0 |  | 0 | 0 | -0.0050583 | 0 |  | 0 | 0
117 |  | Concrete | 85 | 36.6 |  |  | 6.5851 | -177.1024 |  |  | -0.0050188 | 0 |  | 0 | 0 |  | -0.0050253 | 0 |  | 0 | 0 |  | -0.0050303 | 0 |  | 0 | 0 |  | -0.0050342 | 0 |  | 0 | 0 |  | -0.0050375 | 0 |  | 0 | 0 | -0.0050401 | 0 |  | 0 | 0 | -0.0050424 | 0 |  | 0 | 0 | -0.0050443 | 0 |  | 0 | 0 | -0.005046 | 0 |  | 0 | 0 | -0.0050475 | 0 |  | 0 | 0 | -0.0050487 | 0 |  | 0 | 0 | -0.0050499 | 0 |  | 0 | 0 | -0.0050509 | 0 |  | 0 | 0 | -0.0050518 | 0 |  | 0 | 0 | -0.0050526 | 0 |  | 0 | 0 | -0.0050534 | 0 |  | 0 | 0 | -0.0050541 | 0 |  | 0 | 0 | -0.0050547 | 0 |  | 0 | 0 | -0.0050553 | 0 |  | 0 | 0 | -0.0050558 | 0 |  | 0 | 0 | -0.0050563 | 0 |  | 0 | 0
118 |  | Concrete | 86 | 36.6 |  |  | 1.8006 | -176.7166 |  |  | -0.0050108 | 0 |  | 0 | 0 |  | -0.0050183 | 0 |  | 0 | 0 |  | -0.0050241 | 0 |  | 0 | 0 |  | -0.0050287 | 0 |  | 0 | 0 |  | -0.0050324 | 0 |  | 0 | 0 | -0.0050355 | 0 |  | 0 | 0 | -0.0050381 | 0 |  | 0 | 0 | -0.0050404 | 0 |  | 0 | 0 | -0.0050423 | 0 |  | 0 | 0 | -0.005044 | 0 |  | 0 | 0 | -0.0050455 | 0 |  | 0 | 0 | -0.0050468 | 0 |  | 0 | 0 | -0.005048 | 0 |  | 0 | 0 | -0.0050491 | 0 |  | 0 | 0 | -0.00505 | 0 |  | 0 | 0 | -0.0050509 | 0 |  | 0 | 0 | -0.0050517 | 0 |  | 0 | 0 | -0.0050524 | 0 |  | 0 | 0 | -0.0050531 | 0 |  | 0 | 0 | -0.0050537 | 0 |  | 0 | 0 | -0.0050543 | 0 |  | 0 | 0
119 |  | Concrete | 87 | 36.6 |  |  | -2.9839 | -176.3308 |  |  | -0.0050027 | 0 |  | 0 | 0 |  | -0.0050113 | 0 |  | 0 | 0 |  | -0.0050179 | 0 |  | 0 | 0 |  | -0.0050231 | 0 |  | 0 | 0 |  | -0.0050274 | 0 |  | 0 | 0 | -0.0050309 | 0 |  | 0 | 0 | -0.0050339 | 0 |  | 0 | 0 | -0.0050364 | 0 |  | 0 | 0 | -0.0050386 | 0 |  | 0 | 0 | -0.0050406 | 0 |  | 0 | 0 | -0.0050423 | 0 |  | 0 | 0 | -0.0050438 | 0 |  | 0 | 0 | -0.0050451 | 0 |  | 0 | 0 | -0.0050463 | 0 |  | 0 | 0 | -0.0050474 | 0 |  | 0 | 0 | -0.0050484 | 0 |  | 0 | 0 | -0.0050493 | 0 |  | 0 | 0 | -0.0050501 | 0 |  | 0 | 0 | -0.0050509 | 0 |  | 0 | 0 | -0.0050516 | 0 |  | 0 | 0 | -0.0050522 | 0 |  | 0 | 0
120 |  | Concrete | 88 | 36.6 |  |  | -7.7683 | -175.9449 |  |  | -0.0049947 | 0 |  | 0 | 0 |  | -0.0050043 | 0 |  | 0 | 0 |  | -0.0050116 | 0 |  | 0 | 0 |  | -0.0050175 | 0 |  | 0 | 0 |  | -0.0050223 | 0 |  | 0 | 0 | -0.0050263 | 0 |  | 0 | 0 | -0.0050296 | 0 |  | 0 | 0 | -0.0050325 | 0 |  | 0 | 0 | -0.0050349 | 0 |  | 0 | 0 | -0.0050371 | 0 |  | 0 | 0 | -0.005039 | 0 |  | 0 | 0 | -0.0050407 | 0 |  | 0 | 0 | -0.0050422 | 0 |  | 0 | 0 | -0.0050436 | 0 |  | 0 | 0 | -0.0050448 | 0 |  | 0 | 0 | -0.0050459 | 0 |  | 0 | 0 | -0.0050469 | 0 |  | 0 | 0 | -0.0050478 | 0 |  | 0 | 0 | -0.0050487 | 0 |  | 0 | 0 | -0.0050495 | 0 |  | 0 | 0 | -0.0050502 | 0 |  | 0 | 0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
[14 empty] | 1 | [5 empty] | 2 | [5 empty] | 3 | [5 empty] | 4 | [5 empty] | 5 |  |  |  |  | 6 |  |  |  |  | 7 |  |  |  |  | 8 |  |  |  |  | 9 |  |  |  |  | 10 |  |  |  |  | 11 |  |  |  |  | 12 |  |  |  |  | 13 |  |  |  |  | 14 |  |  |  |  | 15 |  |  |  |  | 16 |  |  |  |  | 17 |  |  |  |  | 18 |  |  |  |  | 19 |  |  |  |  | 20 |  |  |  |  | 21
|  | SUM |  | 4244.4433 | [9 empty] | 3350.7768 | 595043.2801 |  |  |  |  | 2828.1111 | 559435.117 |  |  |  |  | 1319.1673 | 321104.5832 |  |  |  |  | -275.6427 | 48882.0565 |  |  |  |  | -451.9112 | 19734.0348 |  |  |  | -493.9817 | 13506.9557 |  |  |  | -526.7581 | 8446.7251 |  |  |  | -552.291 | 4350.9462 |  |  |  | -572.1014 | 1066.0721 |  |  |  | -587.1667 | -1501.3588 |  |  |  | -596.589 | -3135.1567 |  |  |  | -596.6 | -3137.1152 |  |  |  | -596.6 | -3137.1152 |  |  |  | -596.6 | -3137.1152 |  |  |  | -596.6 | -3137.1152 |  |  |  | -596.6 | -3137.1152 |  |  |  | -596.6 | -3137.1152 |  |  |  | -596.6 | -3137.1152 |  |  |  | -596.6 | -3137.1152 |  |  |  | -596.6 | -3137.1152 |  |  |  | -596.6 | -3137.1152
[14 empty] | 595043.2801 | [5 empty] | 559435.117 | [5 empty] | 321104.5832 | [5 empty] | 48882.0565 | [5 empty] | 19734.0348 |  |  |  |  | 13506.9557 |  |  |  |  | 8446.7251 |  |  |  |  | 4350.9462 |  |  |  |  | 1066.0721 |  |  |  |  | -1501.3588 |  |  |  |  | -3135.1567 |  |  |  |  | -3137.1152 |  |  |  |  | -3137.1152 |  |  |  |  | -3137.1152 |  |  |  |  | -3137.1152 |  |  |  |  | -3137.1152 |  |  |  |  | -3137.1152 |  |  |  |  | -3137.1152 |  |  |  |  | -3137.1152 |  |  |  |  | -3137.1152 |  |  |  |  | -3137.1152
R E B A R D A T A
|  | BAR | DIA | As
|  | # | in | sq in
|  | 3 | 0.375 | 0.11
|  | 4 | 0.5 | 0.2
|  | 5 | 0.625 | 0.31
|  | 6 | 0.75 | 0.44
|  | 7 | 0.875 | 0.6
|  | 8 | 1 | 0.79
|  | 9 | 1.128 | 1
|  | 10 | 1.27 | 1.27
|  | 11 | 1.41 | 1.56
|  | 14 | 1.693 | 2.25
|  | 18 | 2.257 | 4

## P-M, ASD (hidden)
Fb = | 1.32 | ksi, (TMS 2-17) |  |  |  | Angle = | 4.6106 | deg | [10 empty] | R E I N F O R C E M E N T
Fs = | 32 | ksi, (TMS 2.3.2.1) | [16 empty] | BAR | DIAM | As
Em = | 2700 | ksi, (TMS 1.8.2.2.1) |  |  |  | te = | t - | 0.375 | [10 empty] | # | in | in2
Es = | 29000 | ksi, (TMS 1.8.2.1) | [16 empty] | 3 | 0.375 | 0.11
Lw = | 30 | ft, (within vertical control joints) | [16 empty] | 4 | 0.5 | 0.2
[19 empty] | 5 | 0.625 | 0.31
tw = | 8 | in | 2 | # | 6 | at each ends, with |  | 8 | in center to edge. | [9 empty] | 6 | 0.75 | 0.44
| Ash, Horizontal | 1 | # | 6 | @ | 16 | in o.c. | [11 empty] | 7 | 0.875 | 0.6
| Asv, Vertical | 1 | # | 6 | @ | 24 | in o.c. | [11 empty] | 8 | 1 | 0.79
[19 empty] | 9 | 1.128 | 1
|  |  | b11 = | 48 | in , | b12 = | 24 | in , | bf1 = | 80 | in ,(TMS 1.9.4.2.3) | [7 empty] | 10 | 1.27 | 1.27
tf1 = | 12 | in , | 2 | # | 5 | @ | 48 | in o.c., Vertical | [10 empty] | 11 | 1.41 | 1.56
[19 empty] | 14 | 1.693 | 2.25
|  |  | b21 = | 36 | in , | b22 = | 48 | in , | bf2 = | 92 | in, (TMS 1.9.4.2.3) | [7 empty] | 18 | 2.257 | 4
tf2 = | 8 | in , | 2 | # | 5 | @ | 48 | in o.c., Vertical
P
|  |  | C | P | M | -318.1867
| 1 | Pure T | 0 | -318.1867 | 0 | -156.3162
| 2 |  | 1e-05 | -156.3162 | 1189.4002 | -112.8161
| 3 |  | 13.9331 | -112.8161 | 1783.6603 | 13.2388
| 4 |  | 27.8663 | 13.2388 | 3567.2843 | 163.2678
| 5 |  | 41.7994 | 163.2678 | 5674.8785 | 341.2028
| 6 |  | 55.7325 | 341.2028 | 8143.0638 | 551.0581 |  |  | P | M
| 7 |  | 69.6657 | 551.0581 | 11005.2488 | 796.8052 |  |  | 163.2678 | 5674.8785
| 8 |  | 83.5988 | 796.8052 | 14294.6822 | 1084.2619 |  |  | 300 | 7571.5285
| 9 |  | 97.5319 | 1084.2619 | 18062.869 | 1421.564 |  |  | 341.2028 | 8143.0638
| 10 | C = Cb | 111.465 | 1421.564 | 22375.8904 | 1645.2501
| 11 |  | 142.91 | 1645.2501 | 23552.1021 | 1843.9508
| 12 |  | 174.355 | 1843.9508 | 24492.836 | 2029.1188
| 13 |  | 205.8 | 2029.1188 | 25182.7851 | 2206.1352
| 14 |  | 237.245 | 2206.1352 | 25614.7577 | 2378.0799
| 15 |  | 268.69 | 2378.0799 | 25783.369 | 2546.4912
| 16 |  | 300.135 | 2546.4912 | 25685.8437 | 2712.2482
| 17 |  | 331.58 | 2712.2482 | 25321.9621 | 2883.9761
| 18 | C = d | 363.025 | 2883.9761 | 24575.8055 | 3425.0889
| 19 |  | 453.7813 | 3425.0889 | 20394.614 | 3785.8307
| 20 |  | 544.5375 | 3785.8307 | 17607.1529 | 4043.5035
| 21 |  | 635.2938 | 4043.5035 | 15616.1093 | 4236.758
| 22 |  | 726.05 | 4236.758 | 14122.8266 | 4387.0672
| 23 |  | 816.8063 | 4387.0672 | 12961.3845 | 4507.3144
| 24 |  | 907.5625 | 4507.3144 | 12032.2309 | 4605.6986
| 25 |  | 998.3188 | 4605.6986 | 11272.0142 | 4687.6854
| 26 |  | 1089.075 | 4687.6854 | 10638.5003
| 27 | Pure C |  | 2069.5566 | 25783.369
|  |  |  | 2069.5566 | 0
[12 empty] | 2 |  |  |  |  | 3 |  |  |  |  | 4 |  |  |  |  | 5 |  |  |  |  | 6 |  |  |  |  | 7 |  |  |  |  | 8 |  |  |  |  | 9 |  |  |  |  | 10 |  |  |  |  | 11 |  |  |  |  | 12 |  |  |  |  | 13 |  |  |  |  | 14 |  |  |  |  | 15 |  |  |  |  | 16 |  |  |  |  | 17 |  |  |  |  | 18 |  |  |  |  | 19 |  |  |  |  | 20 |  |  |  |  | 21 |  |  |  |  | 22 |  |  |  |  | 23 |  |  |  |  | 24 |  |  |  |  | 25 |  |  |  |  | 26
[11 empty] | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in
[6 empty] | Xc | Yc | X | Y |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in |  |  | Cb = | 111.455 | in
[6 empty] | -52 | 180 | -37.3626 | 183.5975 |  | C = | 1e-05 | in |  |  | C = | 13.9331 | in |  |  | C = | 27.8663 | in |  |  | C = | 41.7994 | in |  |  | C = | 55.7325 | in |  |  | C = | 69.6657 | in |  |  | C = | 83.5988 | in |  |  | C = | 97.5319 | in |  |  | C = | 111.465 | in |  |  | C = | 142.91 | in |  |  | C = | 174.355 | in |  |  | C = | 205.8 | in |  |  | C = | 237.245 | in |  |  | C = | 268.69 | in |  |  | C = | 300.135 | in |  |  | C = | 331.58 | in |  |  | C = | 363.025 | in |  |  | C = | 453.7813 | in |  |  | C = | 544.5375 | in |  |  | C = | 635.2938 | in |  |  | C = | 726.05 | in |  |  | C = | 816.8063 | in |  |  | C = | 907.5625 | in |  |  | C = | 998.3188 | in |  |  | C = | 1089.075 | in
[5 empty] | Corner | 28 | 180 | 42.3785 | 177.1668 |  | fb = | 8.2071e-08 | ksi |  |  | fb = | 0.11892 | ksi |  |  | fb = | 0.24772 | ksi |  |  | fb = | 0.38769 | ksi |  |  | fb = | 0.54036 | ksi |  |  | fb = | 0.70754 | ksi |  |  | fb = | 0.89138 | ksi |  |  | fb = | 1.0945 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi |  |  | fb = | 1.32 | ksi
[6 empty] | -40 | -180 | -54.3397 | -176.2021 |  | fs = | 32 | ksi |  |  | fs = | 32 | ksi |  |  | fs = | 32 | ksi |  |  | fs = | 32 | ksi |  |  | fs = | 32 | ksi |  |  | fs = | 32 | ksi |  |  | fs = | 32 | ksi |  |  | fs = | 32 | ksi |  |  | fs = | 31.9959 | ksi |  |  | fs = | 21.8361 | ksi |  |  | fs = | 15.341 | ksi |  |  | fs = | 10.8307 | ksi |  |  | fs = | 7.516 | ksi |  |  | fs = | 4.9772 | ksi |  |  | fs = | 2.9703 | ksi |  |  | fs = | 1.3441 | ksi |  |  | fs = | -0.00039055 | ksi |  |  | fs = | -2.8359 | ksi |  |  | fs = | -4.7262 | ksi |  |  | fs = | -6.0764 | ksi |  |  | fs = | -7.0891 | ksi |  |  | fs = | -7.8767 | ksi |  |  | fs = | -8.5068 | ksi |  |  | fs = | -9.0224 | ksi |  |  | fs = | -9.452 | ksi
[6 empty] | 52 | -180 | 37.3626 | -183.5975 |  | P = | -156.3162 | kips |  |  | P = | -112.8161 | kips |  |  | P = | 13.2388 | kips |  |  | P = | 163.2678 | kips |  |  | P = | 341.2028 | kips |  |  | P = | 551.0581 | kips |  |  | P = | 796.8052 | kips |  |  | P = | 1084.2619 | kips |  |  | P = | 1421.564 | kips |  |  | P = | 1645.2501 | kips |  |  | P = | 1843.9508 | kips |  |  | P = | 2029.1188 | kips |  |  | P = | 2206.1352 | kips |  |  | P = | 2378.0799 | kips |  |  | P = | 2546.4912 | kips |  |  | P = | 2712.2482 | kips |  |  | P = | 2883.9761 | kips |  |  | P = | 3425.0889 | kips |  |  | P = | 3785.8307 | kips |  |  | P = | 4043.5035 | kips |  |  | P = | 4236.758 | kips |  |  | P = | 4387.0672 | kips |  |  | P = | 4507.3144 | kips |  |  | P = | 4605.6986 | kips |  |  | P = | 4687.6854 | kips
[11 empty] | M = | 1189.4002 | ft-k |  |  | M = | 1783.6603 | ft-k |  |  | M = | 3567.2843 | ft-k |  |  | M = | 5674.8785 | ft-k |  |  | M = | 8143.0638 | ft-k |  |  | M = | 11005.2488 | ft-k |  |  | M = | 14294.6822 | ft-k |  |  | M = | 18062.869 | ft-k |  |  | M = | 22375.8904 | ft-k |  |  | M = | 23552.1021 | ft-k |  |  | M = | 24492.836 | ft-k |  |  | M = | 25182.7851 | ft-k |  |  | M = | 25614.7577 | ft-k |  |  | M = | 25783.369 | ft-k |  |  | M = | 25685.8437 | ft-k |  |  | M = | 25321.9621 | ft-k |  |  | M = | 24575.8055 | ft-k |  |  | M = | 20394.614 | ft-k |  |  | M = | 17607.1529 | ft-k |  |  | M = | 15616.1093 | ft-k |  |  | M = | 14122.8266 | ft-k |  |  | M = | 12961.3845 | ft-k |  |  | M = | 12032.2309 | ft-k |  |  | M = | 11272.0142 | ft-k |  |  | M = | 10638.5003 | ft-k
|  | b | h | Am | As | Xc | Yc | X | Y |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M
| 1 | 4.8 | 11.625 | 55.8 | 0.062 | -49.6 | 174 | -35.4526 | 177.424 |  | -0.050667 | 0.5442 | -0.03374 | -0.49886 |  | 0.066226 | -0.71132 | 3.6954 | 54.638 |  | 0.19284 | -2.0712 | 10.7604 | 159.0956 |  | 0.33043 | -3.5491 | 18.4382 | 272.6152 |  | 0.48051 | -5.161 | 26.8123 | 396.4295 |  | 0.64484 | -6.926 | 35.982 | 532.0052 |  | 0.82556 | -8.8671 | 46.0661 | 681.102 |  | 1.0252 | -11.0119 | 57.2086 | 845.8487 |  | 1.2469 | -13.3925 | 69.5766 | 1028.7124 |  | 1.263 | -13.5653 | 70.4742 | 1041.984 |  | 1.2733 | -13.6758 | 71.048 | 1050.4685 |  | 1.2804 | -13.7525 | 71.4465 | 1056.3602 |  | 1.2857 | -13.8088 | 71.7393 | 1060.6901 |  | 1.2897 | -13.852 | 71.9637 | 1064.0066 |  | 1.2928 | -13.8862 | 72.141 | 1066.6281 |  | 1.2954 | -13.9138 | 72.2846 | 1068.7524 |  | 1.2976 | -13.9367 | 72.4034 | 1070.5087 |  | 1.302 | -13.9849 | 72.6539 | 1074.2126 |  | 1.305 | -14.017 | 72.821 | 1076.6819 |  | 1.3072 | -14.04 | 72.9402 | 1078.4457 |  | 1.3088 | -14.0572 | 73.0297 | 1079.7686 |  | 1.31 | -14.0706 | 73.0993 | 1080.7974 |  | 1.311 | -14.0813 | 73.155 | 1081.6205 |  | 1.3118 | -14.0901 | 73.2005 | 1082.294 |  | 1.3125 | -14.0974 | 73.2385 | 1082.8552
| 2 | 4.8 | 11.625 | 55.8 | 0.062 | -44.8 | 174 | -30.6682 | 177.0381 |  | -0.053833 | 0.57821 | -0.035849 | -0.52889 |  | 0.062933 | -0.67595 | 3.5117 | 51.8083 |  | 0.18941 | -2.0344 | 10.569 | 155.926 |  | 0.32686 | -3.5107 | 18.2385 | 269.0762 |  | 0.47677 | -5.1208 | 26.6036 | 392.4876 |  | 0.64092 | -6.8839 | 35.7633 | 527.6223 |  | 0.82144 | -8.8229 | 45.8365 | 676.234 |  | 1.0209 | -10.9654 | 56.967 | 840.4446 |  | 1.2423 | -13.3435 | 69.3216 | 1022.7137 |  | 1.2594 | -13.527 | 70.2753 | 1036.7841 |  | 1.2703 | -13.6444 | 70.885 | 1045.7792 |  | 1.2779 | -13.7259 | 71.3084 | 1052.0256 |  | 1.2835 | -13.7858 | 71.6196 | 1056.6161 |  | 1.2878 | -13.8317 | 71.8579 | 1060.1322 |  | 1.2912 | -13.8679 | 72.0463 | 1062.9115 |  | 1.2939 | -13.8973 | 72.1989 | 1065.1637 |  | 1.2961 | -13.9216 | 72.3251 | 1067.0257 |  | 1.3009 | -13.9728 | 72.5913 | 1070.9526 |  | 1.3041 | -14.007 | 72.7688 | 1073.5705 |  | 1.3064 | -14.0314 | 72.8955 | 1075.4404 |  | 1.3081 | -14.0497 | 72.9906 | 1076.8429 |  | 1.3094 | -14.0639 | 73.0645 | 1077.9337 |  | 1.3105 | -14.0753 | 73.1237 | 1078.8063 |  | 1.3113 | -14.0846 | 73.1721 | 1079.5203 |  | 1.312 | -14.0924 | 73.2124 | 1080.1153
| 3 | 4.8 | 11.625 | 55.8 | 0.062 | -40 | 174 | -25.8837 | 176.6523 |  | -0.057 | 0.61222 | -0.037958 | -0.55878 |  | 0.05964 | -0.64058 | 3.3279 | 48.9903 |  | 0.18598 | -1.9975 | 10.3776 | 152.7687 |  | 0.32328 | -3.4722 | 18.0388 | 265.5501 |  | 0.47303 | -5.0806 | 26.3949 | 388.5592 |  | 0.637 | -6.8419 | 35.5446 | 523.2534 |  | 0.81733 | -8.7787 | 45.6069 | 671.3807 |  | 1.0166 | -10.9189 | 56.7254 | 835.0561 |  | 1.2378 | -13.2944 | 69.0666 | 1016.7314 |  | 1.2559 | -13.4888 | 70.0764 | 1031.597 |  | 1.2674 | -13.613 | 70.722 | 1041.1005 |  | 1.2755 | -13.6993 | 71.1703 | 1047.6999 |  | 1.2814 | -13.7627 | 71.4998 | 1052.5499 |  | 1.2859 | -13.8113 | 71.7521 | 1056.2646 |  | 1.2895 | -13.8497 | 71.9516 | 1059.201 |  | 1.2924 | -13.8808 | 72.1132 | 1061.5805 |  | 1.2947 | -13.9065 | 72.2469 | 1063.5477 |  | 1.2998 | -13.9608 | 72.5287 | 1067.6965 |  | 1.3032 | -13.997 | 72.7166 | 1070.4624 |  | 1.3056 | -14.0228 | 72.8508 | 1072.438 |  | 1.3074 | -14.0422 | 72.9514 | 1073.9198 |  | 1.3088 | -14.0572 | 73.0297 | 1075.0722 |  | 1.3099 | -14.0693 | 73.0923 | 1075.9942 |  | 1.3108 | -14.0791 | 73.1436 | 1076.7485 |  | 1.3116 | -14.0874 | 73.1863 | 1077.3771
| 4 | 4.8 | 11.625 | 55.8 | 0.062 | -35.2 | 174 | -21.0992 | 176.2665 |  | -0.060167 | 0.64623 | -0.040067 | -0.58853 |  | 0.056347 | -0.60521 | 3.1442 | 46.1842 |  | 0.18255 | -1.9607 | 10.1862 | 149.6237 |  | 0.3197 | -3.4338 | 17.8391 | 262.0368 |  | 0.46928 | -5.0405 | 26.1861 | 384.6443 |  | 0.63308 | -6.7998 | 35.326 | 518.8986 |  | 0.81321 | -8.7345 | 45.3774 | 666.5422 |  | 1.0123 | -10.8724 | 56.4838 | 829.6831 |  | 1.2332 | -13.2453 | 68.8117 | 1010.7655 |  | 1.2523 | -13.4505 | 69.8776 | 1026.4227 |  | 1.2645 | -13.5817 | 70.559 | 1036.4323 |  | 1.273 | -13.6727 | 71.0322 | 1043.383 |  | 1.2792 | -13.7397 | 71.38 | 1048.4913 |  | 1.284 | -13.7909 | 71.6463 | 1052.4039 |  | 1.2878 | -13.8315 | 71.8569 | 1055.4966 |  | 1.2908 | -13.8643 | 72.0275 | 1058.0028 |  | 1.2933 | -13.8915 | 72.1686 | 1060.0748 |  | 1.2987 | -13.9487 | 72.4661 | 1064.4445 |  | 1.3022 | -13.9869 | 72.6644 | 1067.3577 |  | 1.3048 | -14.0142 | 72.806 | 1069.4385 |  | 1.3067 | -14.0346 | 72.9123 | 1070.9991 |  | 1.3082 | -14.0505 | 72.9949 | 1072.2129 |  | 1.3093 | -14.0633 | 73.061 | 1073.184 |  | 1.3103 | -14.0737 | 73.1151 | 1073.9785 |  | 1.3111 | -14.0823 | 73.1602 | 1074.6406
b11 | 5 | 4.8 | 11.625 | 55.8 | 0.062 | -30.4 | 174 | -16.3148 | 175.8806 | b11 | -0.063333 | 0.68025 | -0.042175 | -0.61815 | b11 | 0.053054 | -0.56984 | 2.9604 | 43.3899 | b11 | 0.17912 | -1.9239 | 9.9948 | 146.491 | b11 | 0.31612 | -3.3954 | 17.6394 | 258.5364 | b11 | 0.46554 | -5.0003 | 25.9774 | 380.7427 | b11 | 0.62916 | -6.7577 | 35.1073 | 514.5579 | b11 | 0.8091 | -8.6903 | 45.1478 | 661.7184 | b11 | 1.0079 | -10.8259 | 56.2422 | 824.3256 | b11 | 1.2286 | -13.1962 | 68.5567 | 1004.816 | b11 | 1.2487 | -13.4122 | 69.6787 | 1021.2612 | b11 | 1.2616 | -13.5503 | 70.396 | 1031.7745 | b11 | 1.2705 | -13.6462 | 70.8941 | 1039.0751 | b11 | 1.2771 | -13.7166 | 71.2602 | 1044.4404 | b11 | 1.2821 | -13.7706 | 71.5406 | 1048.5499 | b11 | 1.2861 | -13.8132 | 71.7622 | 1051.7983 | b11 | 1.2893 | -13.8478 | 71.9418 | 1054.4306 | b11 | 1.2919 | -13.8764 | 72.0903 | 1056.6069 | b11 | 1.2976 | -13.9367 | 72.4034 | 1061.1965 | b11 | 1.3013 | -13.9769 | 72.6122 | 1064.2563 | b11 | 1.304 | -14.0056 | 72.7613 | 1066.4419 | b11 | 1.306 | -14.0271 | 72.8731 | 1068.081 | b11 | 1.3075 | -14.0438 | 72.9601 | 1069.3559 | b11 | 1.3088 | -14.0572 | 73.0297 | 1070.3759 | b11 | 1.3098 | -14.0682 | 73.0866 | 1071.2103 | b11 | 1.3106 | -14.0773 | 73.1341 | 1071.9057
| 6 | 4.8 | 11.625 | 55.8 | 0.062 | -25.6 | 174 | -11.5303 | 175.4948 |  | -0.0665 | 0.71426 | -0.044284 | -0.64764 |  | 0.049761 | -0.53447 | 2.7767 | 40.6074 |  | 0.17569 | -1.887 | 9.8034 | 143.3706 |  | 0.31254 | -3.3569 | 17.4398 | 255.0488 |  | 0.4618 | -4.9601 | 25.7686 | 376.8546 |  | 0.62524 | -6.7156 | 34.8886 | 510.2312 |  | 0.80499 | -8.6461 | 44.9182 | 656.9094 |  | 1.0036 | -10.7793 | 56.0006 | 818.9837 |  | 1.224 | -13.1472 | 68.3017 | 998.8829 |  | 1.2452 | -13.3739 | 69.4798 | 1016.1124 |  | 1.2587 | -13.5189 | 70.233 | 1027.1272 |  | 1.268 | -13.6196 | 70.756 | 1034.776 |  | 1.2749 | -13.6936 | 71.1404 | 1040.3973 |  | 1.2802 | -13.7502 | 71.4348 | 1044.7028 |  | 1.2844 | -13.795 | 71.6675 | 1048.1061 |  | 1.2877 | -13.8313 | 71.8561 | 1050.8639 |  | 1.2905 | -13.8613 | 72.012 | 1053.144 |  | 1.2964 | -13.9246 | 72.3408 | 1057.9526 |  | 1.3004 | -13.9668 | 72.56 | 1061.1583 |  | 1.3032 | -13.997 | 72.7166 | 1063.4481 |  | 1.3053 | -14.0196 | 72.834 | 1065.1654 |  | 1.3069 | -14.0371 | 72.9253 | 1066.5012 |  | 1.3082 | -14.0512 | 72.9984 | 1067.5697 |  | 1.3093 | -14.0627 | 73.0582 | 1068.444 |  | 1.3102 | -14.0723 | 73.108 | 1069.1726
| 7 | 4.8 | 11.625 | 55.8 | 0.062 | -20.8 | 174 | -6.7458 | 175.1089 |  | -0.069667 | 0.74827 | -0.046393 | -0.67698 |  | 0.046468 | -0.4991 | 2.5929 | 37.8367 |  | 0.17226 | -1.8502 | 9.612 | 140.2625 |  | 0.30896 | -3.3185 | 17.2401 | 251.574 |  | 0.45806 | -4.9199 | 25.5599 | 372.9799 |  | 0.62133 | -6.6735 | 34.67 | 505.9185 |  | 0.80087 | -8.602 | 44.6887 | 652.1152 |  | 0.99926 | -10.7328 | 55.7589 | 813.6573 |  | 1.2195 | -13.0981 | 68.0468 | 992.9662 |  | 1.2416 | -13.3356 | 69.281 | 1010.9765 |  | 1.2557 | -13.4875 | 70.07 | 1022.4904 |  | 1.2656 | -13.593 | 70.6179 | 1030.4858 |  | 1.2728 | -13.6705 | 71.0206 | 1036.3618 |  | 1.2783 | -13.7299 | 71.329 | 1040.8624 |  | 1.2827 | -13.7768 | 71.5728 | 1044.42 |  | 1.2862 | -13.8148 | 71.7704 | 1047.3028 |  | 1.2891 | -13.8463 | 71.9337 | 1049.6862 |  | 1.2953 | -13.9126 | 72.2782 | 1054.7127 |  | 1.2994 | -13.9568 | 72.5078 | 1058.0636 |  | 1.3024 | -13.9883 | 72.6718 | 1060.4572 |  | 1.3046 | -14.012 | 72.7949 | 1062.2524 |  | 1.3063 | -14.0304 | 72.8905 | 1063.6486 |  | 1.3077 | -14.0452 | 72.9671 | 1064.7656 |  | 1.3088 | -14.0572 | 73.0297 | 1065.6795 |  | 1.3097 | -14.0673 | 73.0819 | 1066.4411
| 8 | 4.8 | 11.625 | 55.8 | 0.062 | -16 | 174 | -1.9614 | 174.7231 |  | -0.072833 | 0.78228 | -0.048502 | -0.7062 |  | 0.043175 | -0.46373 | 2.4091 | 35.0778 |  | 0.16883 | -1.8133 | 9.4206 | 137.1667 |  | 0.30538 | -3.28 | 17.0404 | 248.1121 |  | 0.45432 | -4.8797 | 25.3511 | 369.1186 |  | 0.61741 | -6.6314 | 34.4513 | 501.62 |  | 0.79676 | -8.5578 | 44.4591 | 647.3358 |  | 0.99493 | -10.6863 | 55.5173 | 808.3465 |  | 1.2149 | -13.049 | 67.7918 | 987.0659 |  | 1.238 | -13.2974 | 69.0821 | 1005.8533 |  | 1.2528 | -13.4561 | 69.907 | 1017.8641 |  | 1.2631 | -13.5664 | 70.4798 | 1026.2045 |  | 1.2706 | -13.6474 | 70.9008 | 1032.334 |  | 1.2764 | -13.7095 | 71.2233 | 1037.0289 |  | 1.281 | -13.7586 | 71.4781 | 1040.7399 |  | 1.2847 | -13.7983 | 71.6847 | 1043.7472 |  | 1.2877 | -13.8312 | 71.8554 | 1046.2334 |  | 1.2942 | -13.9005 | 72.2155 | 1051.4768 |  | 1.2985 | -13.9467 | 72.4556 | 1054.9723 |  | 1.3016 | -13.9797 | 72.6271 | 1057.4692 |  | 1.3039 | -14.0045 | 72.7557 | 1059.3418 |  | 1.3057 | -14.0237 | 72.8557 | 1060.7983 |  | 1.3071 | -14.0391 | 72.9358 | 1061.9635 |  | 1.3083 | -14.0517 | 73.0012 | 1062.9168 |  | 1.3092 | -14.0622 | 73.0558 | 1063.7113
| 9 | 4.8 | 11.625 | 55.8 | 0.062 | -11.2 | 174 | 2.8231 | 174.3372 |  | -0.076 | 0.8163 | -0.05061 | -0.73527 |  | 0.039882 | -0.42836 | 2.2254 | 32.3308 |  | 0.1654 | -1.7765 | 9.2292 | 134.0832 |  | 0.3018 | -3.2416 | 16.8407 | 244.663 |  | 0.45058 | -4.8396 | 25.1424 | 365.2707 |  | 0.61349 | -6.5893 | 34.2327 | 497.3355 |  | 0.79264 | -8.5136 | 44.2295 | 642.5711 |  | 0.9906 | -10.6398 | 55.2757 | 803.0512 |  | 1.2103 | -12.9999 | 67.5368 | 981.182 |  | 1.2345 | -13.2591 | 68.8833 | 1000.7429 |  | 1.2499 | -13.4248 | 69.744 | 1013.2483 |  | 1.2606 | -13.5398 | 70.3417 | 1021.9321 |  | 1.2685 | -13.6244 | 70.781 | 1028.314 |  | 1.2745 | -13.6891 | 71.1175 | 1033.2021 |  | 1.2793 | -13.7403 | 71.3834 | 1037.066 |  | 1.2831 | -13.7818 | 71.599 | 1040.197 |  | 1.2863 | -13.8161 | 71.7771 | 1042.7856 |  | 1.2931 | -13.8885 | 72.1529 | 1048.2449 |  | 1.2976 | -13.9367 | 72.4034 | 1051.8844 |  | 1.3008 | -13.9711 | 72.5824 | 1054.484 |  | 1.3032 | -13.997 | 72.7166 | 1056.4338 |  | 1.305 | -14.017 | 72.821 | 1057.9502 |  | 1.3065 | -14.0331 | 72.9045 | 1059.1634 |  | 1.3078 | -14.0463 | 72.9728 | 1060.156 |  | 1.3088 | -14.0572 | 73.0297 | 1060.9832
| 10 | 4.8 | 11.625 | 55.8 | 0.062 | -6.4 | 174 | 7.6076 | 173.9514 |  | -0.079167 | 0.85031 | -0.052719 | -0.76421 |  | 0.036589 | -0.39299 | 2.0416 | 29.5956 |  | 0.16197 | -1.7397 | 9.0378 | 131.0121 |  | 0.29823 | -3.2032 | 16.641 | 241.2267 |  | 0.44684 | -4.7994 | 24.9336 | 361.4363 |  | 0.60957 | -6.5472 | 34.014 | 493.065 |  | 0.78853 | -8.4694 | 44 | 637.8211 |  | 0.98627 | -10.5933 | 55.0341 | 797.7714 |  | 1.2058 | -12.9508 | 67.2819 | 975.3145 |  | 1.2309 | -13.2208 | 68.6844 | 995.6454 |  | 1.247 | -13.3934 | 69.581 | 1008.6429 |  | 1.2581 | -13.5132 | 70.2037 | 1017.6686 |  | 1.2663 | -13.6013 | 70.6612 | 1024.3016 |  | 1.2726 | -13.6688 | 71.0117 | 1029.3822 |  | 1.2776 | -13.7221 | 71.2888 | 1033.3981 |  | 1.2816 | -13.7653 | 71.5132 | 1036.6524 |  | 1.2849 | -13.8011 | 71.6989 | 1039.3429 |  | 1.2919 | -13.8764 | 72.0903 | 1045.017 |  | 1.2966 | -13.9266 | 72.3512 | 1048.7998 |  | 1.3 | -13.9625 | 72.5376 | 1051.5018 |  | 1.3025 | -13.9894 | 72.6774 | 1053.5283 |  | 1.3044 | -14.0103 | 72.7862 | 1055.1044 |  | 1.306 | -14.0271 | 72.8731 | 1056.3653 |  | 1.3072 | -14.0408 | 72.9443 | 1057.397 |  | 1.3083 | -14.0522 | 73.0036 | 1058.2567
| 1 | 2.4 | 11.625 | 27.9 | 0.062 | 26.8 | 174 | 40.7001 | 171.2826 |  | -0.10107 | 1.0856 | -0.067305 | -0.96068 |  | 0.013812 | -0.14835 | 0.38534 | 5.5002 |  | 0.13824 | -1.4848 | 3.857 | 55.0534 |  | 0.27347 | -2.9373 | 7.6299 | 108.9055 |  | 0.42096 | -4.5215 | 11.7449 | 167.6412 |  | 0.58247 | -6.2561 | 16.2508 | 231.9564 |  | 0.76007 | -8.1638 | 21.2061 | 302.6858 |  | 0.95632 | -10.2716 | 26.6815 | 380.8392 |  | 1.1742 | -12.6114 | 32.7592 | 467.5898 |  | 1.2063 | -12.956 | 33.6545 | 480.3686 |  | 1.2268 | -13.1764 | 34.2268 | 488.5381 |  | 1.241 | -13.3294 | 34.6243 | 494.2111 |  | 1.2515 | -13.4418 | 34.9163 | 498.3802 |  | 1.2595 | -13.528 | 35.1401 | 501.5736 |  | 1.2658 | -13.596 | 35.3169 | 504.0977 |  | 1.271 | -13.6512 | 35.4602 | 506.1432 |  | 1.2752 | -13.6968 | 35.5787 | 507.8343 |  | 1.2842 | -13.793 | 35.8286 | 511.4007 |  | 1.2901 | -13.8571 | 35.9951 | 513.7783 |  | 1.2944 | -13.9029 | 36.1141 | 515.4766 |  | 1.2976 | -13.9373 | 36.2033 | 516.7503 |  | 1.3001 | -13.964 | 36.2728 | 517.741 |  | 1.3021 | -13.9854 | 36.3283 | 518.5335 |  | 1.3037 | -14.0029 | 36.3737 | 519.182 |  | 1.3051 | -14.0175 | 36.4116 | 519.7224
| 2 | 2.4 | 11.625 | 27.9 | 0.062 | 24.4 | 174 | 38.3079 | 171.4756 |  | -0.099486 | 1.0686 | -0.06625 | -0.94669 |  | 0.015458 | -0.16603 | 0.43128 | 6.1628 |  | 0.13996 | -1.5033 | 3.9049 | 55.7991 |  | 0.27526 | -2.9565 | 7.6798 | 109.7415 |  | 0.42283 | -4.5416 | 11.7971 | 168.5757 |  | 0.58442 | -6.2772 | 16.3054 | 232.9988 |  | 0.76213 | -8.1858 | 21.2634 | 303.8468 |  | 0.95849 | -10.2949 | 26.7419 | 382.1313 |  | 1.1764 | -12.6359 | 32.8229 | 469.0273 |  | 1.208 | -12.9752 | 33.7042 | 481.6201 |  | 1.2282 | -13.1921 | 34.2676 | 489.6706 |  | 1.2422 | -13.3427 | 34.6588 | 495.261 |  | 1.2526 | -13.4534 | 34.9463 | 499.3695 |  | 1.2604 | -13.5381 | 35.1665 | 502.5164 |  | 1.2667 | -13.6052 | 35.3406 | 505.0038 |  | 1.2717 | -13.6595 | 35.4816 | 507.0195 |  | 1.2759 | -13.7044 | 35.5983 | 508.6859 |  | 1.2847 | -13.799 | 35.8442 | 512.2004 |  | 1.2906 | -13.8622 | 36.0082 | 514.5434 |  | 1.2948 | -13.9073 | 36.1253 | 516.217 |  | 1.298 | -13.9411 | 36.2131 | 517.4722 |  | 1.3004 | -13.9674 | 36.2814 | 518.4485 |  | 1.3024 | -13.9884 | 36.3361 | 519.2295 |  | 1.304 | -14.0056 | 36.3808 | 519.8685 |  | 1.3053 | -14.02 | 36.4181 | 520.401
| 3 | 2.4 | 11.625 | 27.9 | 0.062 | 22 | 174 | 35.9157 | 171.6685 |  | -0.097903 | 1.0515 | -0.065196 | -0.93268 |  | 0.017105 | -0.18372 | 0.47722 | 6.827 |  | 0.14167 | -1.5217 | 3.9527 | 56.5464 |  | 0.27705 | -2.9757 | 7.7297 | 110.5792 |  | 0.4247 | -4.5616 | 11.8493 | 169.512 |  | 0.58638 | -6.2982 | 16.3601 | 234.043 |  | 0.76419 | -8.2079 | 21.3208 | 305.0097 |  | 0.96065 | -10.3181 | 26.8023 | 383.4254 |  | 1.1787 | -12.6605 | 32.8867 | 470.4669 |  | 1.2098 | -12.9943 | 33.7539 | 482.8732 |  | 1.2297 | -13.2078 | 34.3083 | 490.8045 |  | 1.2435 | -13.356 | 34.6933 | 496.3121 |  | 1.2536 | -13.4649 | 34.9762 | 500.3598 |  | 1.2614 | -13.5483 | 35.1929 | 503.46 |  | 1.2675 | -13.6143 | 35.3643 | 505.9106 |  | 1.2725 | -13.6677 | 35.5031 | 507.8964 |  | 1.2766 | -13.7119 | 35.6178 | 509.5382 |  | 1.2853 | -13.8051 | 35.8599 | 513.0007 |  | 1.2911 | -13.8672 | 36.0212 | 515.309 |  | 1.2952 | -13.9116 | 36.1365 | 516.9578 |  | 1.2983 | -13.9448 | 36.2229 | 518.1944 |  | 1.3007 | -13.9707 | 36.2901 | 519.1562 |  | 1.3026 | -13.9914 | 36.3439 | 519.9256 |  | 1.3042 | -14.0084 | 36.3879 | 520.5552 |  | 1.3055 | -14.0225 | 36.4246 | 521.0798
| 4 | 2.4 | 11.625 | 27.9 | 0.062 | 19.6 | 174 | 33.5234 | 171.8614 |  | -0.09632 | 1.0345 | -0.064142 | -0.91862 |  | 0.018751 | -0.2014 | 0.52316 | 7.4925 |  | 0.14339 | -1.5401 | 4.0006 | 57.2952 |  | 0.27884 | -2.995 | 7.7796 | 111.4185 |  | 0.42658 | -4.5817 | 11.9014 | 170.4499 |  | 0.58834 | -6.3192 | 16.4148 | 235.0889 |  | 0.76624 | -8.23 | 21.3782 | 306.1744 |  | 0.96282 | -10.3414 | 26.8627 | 384.7214 |  | 1.181 | -12.685 | 32.9504 | 471.9085 |  | 1.2116 | -13.0135 | 33.8036 | 484.1279 |  | 1.2311 | -13.2235 | 34.3491 | 491.9397 |  | 1.2447 | -13.3693 | 34.7278 | 497.3643 |  | 1.2547 | -13.4764 | 35.0062 | 501.351 |  | 1.2623 | -13.5585 | 35.2194 | 504.4045 |  | 1.2684 | -13.6234 | 35.3879 | 506.8182 |  | 1.2733 | -13.676 | 35.5245 | 508.7741 |  | 1.2773 | -13.7194 | 35.6374 | 510.3911 |  | 1.2859 | -13.8111 | 35.8755 | 513.8014 |  | 1.2916 | -13.8722 | 36.0343 | 516.075 |  | 1.2956 | -13.9159 | 36.1477 | 517.6989 |  | 1.2987 | -13.9486 | 36.2327 | 518.9169 |  | 1.301 | -13.9741 | 36.2988 | 519.8642 |  | 1.3029 | -13.9944 | 36.3518 | 520.622 |  | 1.3045 | -14.0111 | 36.3951 | 521.2421 |  | 1.3058 | -14.025 | 36.4311 | 521.7588
b12 | 5 | 2.4 | 11.625 | 27.9 | 0.062 | 17.2 | 174 | 31.1312 | 172.0543 | b12 | -0.094736 | 1.0175 | -0.063087 | -0.90454 | b12 | 0.020398 | -0.21909 | 0.5691 | 8.1596 | b12 | 0.1451 | -1.5585 | 4.0484 | 58.0456 | b12 | 0.28063 | -3.0142 | 7.8296 | 112.2593 | b12 | 0.42845 | -4.6018 | 11.9536 | 171.3895 | b12 | 0.5903 | -6.3403 | 16.4694 | 236.1366 | b12 | 0.7683 | -8.2521 | 21.4356 | 307.341 | b12 | 0.96498 | -10.3647 | 26.9231 | 386.0193 | b12 | 1.1833 | -12.7095 | 33.0141 | 473.3521 | b12 | 1.2134 | -13.0326 | 33.8533 | 485.3841 | b12 | 1.2326 | -13.2391 | 34.3898 | 493.0762 | b12 | 1.246 | -13.3826 | 34.7623 | 498.4176 | b12 | 1.2558 | -13.488 | 35.0361 | 502.3432 | b12 | 1.2633 | -13.5687 | 35.2458 | 505.3499 | b12 | 1.2692 | -13.6325 | 35.4116 | 507.7265 | b12 | 1.274 | -13.6842 | 35.5459 | 509.6524 | b12 | 1.278 | -13.727 | 35.657 | 511.2447 | b12 | 1.2864 | -13.8171 | 35.8912 | 514.6027 | b12 | 1.292 | -13.8772 | 36.0473 | 516.8414 | b12 | 1.296 | -13.9202 | 36.1588 | 518.4404 | b12 | 1.299 | -13.9524 | 36.2425 | 519.6397 | b12 | 1.3013 | -13.9774 | 36.3075 | 520.5725 | b12 | 1.3032 | -13.9975 | 36.3596 | 521.3187 | b12 | 1.3047 | -14.0138 | 36.4022 | 521.9292 | b12 | 1.306 | -14.0275 | 36.4377 | 522.438
| 6 | 2.4 | 11.625 | 27.9 | 0.062 | 14.8 | 174 | 28.739 | 172.2472 |  | -0.093153 | 1.0005 | -0.062033 | -0.89042 |  | 0.022044 | -0.23677 | 0.61503 | 8.8282 |  | 0.14682 | -1.5769 | 4.0963 | 58.7975 |  | 0.28242 | -3.0334 | 7.8795 | 113.1018 |  | 0.43032 | -4.6219 | 12.0058 | 172.3307 |  | 0.59226 | -6.3613 | 16.5241 | 237.1861 |  | 0.77036 | -8.2742 | 21.493 | 308.5094 |  | 0.96715 | -10.3879 | 26.9835 | 387.3192 |  | 1.1856 | -12.7341 | 33.0779 | 474.7978 |  | 1.2152 | -13.0517 | 33.903 | 486.642 |  | 1.2341 | -13.2548 | 34.4306 | 494.214 |  | 1.2472 | -13.3958 | 34.7969 | 499.4721 |  | 1.2568 | -13.4995 | 35.0661 | 503.3363 |  | 1.2642 | -13.5789 | 35.2723 | 506.2961 |  | 1.2701 | -13.6416 | 35.4353 | 508.6356 |  | 1.2748 | -13.6925 | 35.5673 | 510.5315 |  | 1.2787 | -13.7345 | 35.6765 | 512.0989 |  | 1.287 | -13.8232 | 35.9068 | 515.4045 |  | 1.2925 | -13.8823 | 36.0604 | 517.6082 |  | 1.2964 | -13.9245 | 36.17 | 519.1823 |  | 1.2994 | -13.9561 | 36.2523 | 520.3628 |  | 1.3017 | -13.9808 | 36.3162 | 521.281 |  | 1.3035 | -14.0005 | 36.3674 | 522.0156 |  | 1.305 | -14.0166 | 36.4093 | 522.6166 |  | 1.3062 | -14.03 | 36.4442 | 523.1175
| 7 | 2.4 | 11.625 | 27.9 | 0.062 | 12.4 | 174 | 26.3467 | 172.4402 |  | -0.09157 | 0.98352 | -0.060979 | -0.87626 |  | 0.023691 | -0.25446 | 0.66097 | 9.4982 |  | 0.14853 | -1.5954 | 4.1441 | 59.5509 |  | 0.28421 | -3.0526 | 7.9294 | 113.9459 |  | 0.43219 | -4.642 | 12.058 | 173.2737 |  | 0.59422 | -6.3824 | 16.5788 | 238.2373 |  | 0.77242 | -8.2963 | 21.5504 | 309.6797 |  | 0.96931 | -10.4112 | 27.0439 | 388.621 |  | 1.1879 | -12.7586 | 33.1416 | 476.2456 |  | 1.2169 | -13.0709 | 33.9528 | 487.9015 |  | 1.2355 | -13.2705 | 34.4713 | 495.3531 |  | 1.2484 | -13.4091 | 34.8314 | 500.5276 |  | 1.2579 | -13.511 | 35.096 | 504.3304 |  | 1.2652 | -13.589 | 35.2987 | 507.2431 |  | 1.2709 | -13.6507 | 35.4589 | 509.5455 |  | 1.2756 | -13.7007 | 35.5888 | 511.4112 |  | 1.2794 | -13.742 | 35.6961 | 512.9537 |  | 1.2875 | -13.8292 | 35.9225 | 516.2067 |  | 1.293 | -13.8873 | 36.0734 | 518.3754 |  | 1.2968 | -13.9288 | 36.1812 | 519.9245 |  | 1.2997 | -13.9599 | 36.2621 | 521.0863 |  | 1.302 | -13.9841 | 36.3249 | 521.9899 |  | 1.3038 | -14.0035 | 36.3752 | 522.7128 |  | 1.3052 | -14.0193 | 36.4164 | 523.3043 |  | 1.3065 | -14.0325 | 36.4507 | 523.7971
| 8 | 2.4 | 11.625 | 27.9 | 0.062 | 10 | 174 | 23.9545 | 172.6331 |  | -0.089986 | 0.96652 | -0.059924 | -0.86207 |  | 0.025337 | -0.27214 | 0.70691 | 10.1697 |  | 0.15025 | -1.6138 | 4.192 | 60.3059 |  | 0.286 | -3.0718 | 7.9793 | 114.7916 |  | 0.43406 | -4.6621 | 12.1102 | 174.2183 |  | 0.59618 | -6.4034 | 16.6334 | 239.2902 |  | 0.77447 | -8.3184 | 21.6078 | 310.8518 |  | 0.97148 | -10.4344 | 27.1043 | 389.9247 |  | 1.1902 | -12.7832 | 33.2054 | 477.6954 |  | 1.2187 | -13.09 | 34.0025 | 489.1626 |  | 1.237 | -13.2862 | 34.5121 | 496.4935 |  | 1.2497 | -13.4224 | 34.8659 | 501.5842 |  | 1.259 | -13.5225 | 35.126 | 505.3255 |  | 1.2661 | -13.5992 | 35.3252 | 508.191 |  | 1.2718 | -13.6598 | 35.4826 | 510.4561 |  | 1.2764 | -13.709 | 35.6102 | 512.2916 |  | 1.2801 | -13.7496 | 35.7157 | 513.8091 |  | 1.2881 | -13.8352 | 35.9382 | 517.0095 |  | 1.2934 | -13.8923 | 36.0865 | 519.1431 |  | 1.2972 | -13.9331 | 36.1924 | 520.667 |  | 1.3001 | -13.9637 | 36.2718 | 521.81 |  | 1.3023 | -13.9875 | 36.3336 | 522.699 |  | 1.3041 | -14.0065 | 36.3831 | 523.4102 |  | 1.3055 | -14.0221 | 36.4235 | 523.9921 |  | 1.3067 | -14.035 | 36.4572 | 524.477
| 9 | 2.4 | 11.625 | 27.9 | 0.062 | 7.6 | 174 | 21.5623 | 172.826 |  | -0.088403 | 0.94951 | -0.05887 | -0.84785 |  | 0.026984 | -0.28983 | 0.75285 | 10.8426 |  | 0.15196 | -1.6322 | 4.2398 | 61.0624 |  | 0.28779 | -3.091 | 8.0293 | 115.6388 |  | 0.43593 | -4.6822 | 12.1624 | 175.1646 |  | 0.59814 | -6.4245 | 16.6881 | 240.3449 |  | 0.77653 | -8.3405 | 21.6652 | 312.0257 |  | 0.97364 | -10.4577 | 27.1647 | 391.2304 |  | 1.1924 | -12.8077 | 33.2691 | 479.1473 |  | 1.2205 | -13.1092 | 34.0522 | 490.4252 |  | 1.2385 | -13.3019 | 34.5528 | 497.6352 |  | 1.2509 | -13.4357 | 34.9004 | 502.642 |  | 1.2601 | -13.5341 | 35.1559 | 506.3215 |  | 1.2671 | -13.6094 | 35.3516 | 509.1398 |  | 1.2726 | -13.669 | 35.5063 | 511.3675 |  | 1.2771 | -13.7172 | 35.6316 | 513.1727 |  | 1.2808 | -13.7571 | 35.7353 | 514.6652 |  | 1.2887 | -13.8412 | 35.9538 | 517.8128 |  | 1.2939 | -13.8973 | 36.0995 | 519.9111 |  | 1.2976 | -13.9374 | 36.2036 | 521.41 |  | 1.3004 | -13.9674 | 36.2816 | 522.5341 |  | 1.3026 | -13.9908 | 36.3423 | 523.4084 |  | 1.3043 | -14.0095 | 36.3909 | 524.1079 |  | 1.3058 | -14.0248 | 36.4306 | 524.6802 |  | 1.3069 | -14.0376 | 36.4638 | 525.1571
| 10 | 2.4 | 11.625 | 27.9 | 0.062 | 5.2 | 174 | 19.17 | 173.0189 |  | -0.08682 | 0.93251 | -0.057815 | -0.8336 |  | 0.02863 | -0.30751 | 0.79879 | 11.5171 |  | 0.15368 | -1.6506 | 4.2877 | 61.8204 |  | 0.28958 | -3.1103 | 8.0792 | 116.4877 |  | 0.4378 | -4.7023 | 12.2146 | 176.1126 |  | 0.6001 | -6.4455 | 16.7428 | 241.4014 |  | 0.77859 | -8.3626 | 21.7226 | 313.2015 |  | 0.97581 | -10.4809 | 27.2251 | 392.5381 |  | 1.1947 | -12.8322 | 33.3328 | 480.6012 |  | 1.2223 | -13.1283 | 34.1019 | 491.6895 |  | 1.2399 | -13.3176 | 34.5936 | 498.7783 |  | 1.2521 | -13.449 | 34.935 | 503.7008 |  | 1.2611 | -13.5456 | 35.1859 | 507.3185 |  | 1.268 | -13.6196 | 35.378 | 510.0894 |  | 1.2735 | -13.6781 | 35.53 | 512.2796 |  | 1.2779 | -13.7255 | 35.6531 | 514.0545 |  | 1.2815 | -13.7646 | 35.7548 | 515.5219 |  | 1.2892 | -13.8473 | 35.9695 | 518.6165 |  | 1.2944 | -13.9024 | 36.1126 | 520.6796 |  | 1.298 | -13.9417 | 36.2148 | 522.1533 |  | 1.3008 | -13.9712 | 36.2914 | 523.2585 |  | 1.3029 | -13.9942 | 36.351 | 524.1181 |  | 1.3046 | -14.0125 | 36.3987 | 524.8058 |  | 1.306 | -14.0275 | 36.4378 | 525.3685 |  | 1.3072 | -14.0401 | 36.4703 | 525.8374
| 1 | 8 | 4 | 32 | 0.22 | 0 | 178 | 14.3084 | 177.424 |  | -0.050667 | 0.5442 | -0.11972 | -1.7702 |  | 0.066226 | -0.71132 | 2.1192 | 31.3336 |  | 0.19284 | -2.0712 | 6.1708 | 91.2376 |  | 0.33043 | -3.5491 | 10.5739 | 156.3385 |  | 0.48051 | -5.161 | 15.3763 | 227.3431 |  | 0.64484 | -6.926 | 20.6348 | 305.0926 |  | 0.82556 | -8.8671 | 26.4178 | 390.5961 |  | 1.0252 | -11.0119 | 32.8078 | 485.0745 |  | 1.2469 | -13.3925 | 39.9005 | 589.9426 |  | 1.263 | -13.5653 | 40.4153 | 597.5535 |  | 1.2733 | -13.6758 | 40.7444 | 602.4192 |  | 1.2804 | -13.7525 | 40.9729 | 605.798 |  | 1.2857 | -13.8088 | 41.1408 | 608.2811 |  | 1.2897 | -13.852 | 41.2695 | 610.183 |  | 1.2928 | -13.8862 | 41.3712 | 611.6864 |  | 1.2954 | -13.9138 | 41.4536 | 612.9046 |  | 1.2976 | -13.9367 | 41.5217 | 613.9118 |  | 1.302 | -13.9849 | 41.6653 | 616.0359 |  | 1.305 | -14.017 | 41.7611 | 617.452 |  | 1.3072 | -14.04 | 41.8295 | 618.4635 |  | 1.3088 | -14.0572 | 41.8808 | 619.2221 |  | 1.31 | -14.0706 | 41.9207 | 619.8121 |  | 1.311 | -14.0813 | 41.9527 | 620.2842 |  | 1.3118 | -14.0901 | 41.9788 | 620.6704 |  | 1.3125 | -14.0974 | 42.0006 | 620.9922
| 2 | 8 | 4 | 32 | 0.22 | 0 | 174 | 13.9868 | 173.4369 |  | -0.083389 | 0.89566 | -0.19704 | -2.8479 |  | 0.032198 | -0.34583 | 1.0303 | 14.8914 |  | 0.1574 | -1.6905 | 5.0366 | 72.795 |  | 0.29345 | -3.1519 | 9.3905 | 135.7219 |  | 0.44185 | -4.7458 | 14.1392 | 204.3553 |  | 0.60434 | -6.4911 | 19.339 | 279.5085 |  | 0.78304 | -8.4105 | 25.0574 | 362.1567 |  | 0.9805 | -10.5313 | 31.376 | 453.4801 |  | 1.1997 | -12.8854 | 38.3896 | 554.8482 |  | 1.2262 | -13.1698 | 39.2368 | 567.093 |  | 1.2431 | -13.3516 | 39.7785 | 574.9211 |  | 1.2548 | -13.4778 | 40.1546 | 580.3571 |  | 1.2635 | -13.5706 | 40.431 | 584.352 |  | 1.2701 | -13.6416 | 40.6427 | 587.4119 |  | 1.2753 | -13.6978 | 40.81 | 589.8306 |  | 1.2796 | -13.7433 | 40.9456 | 591.7906 |  | 1.2831 | -13.781 | 41.0578 | 593.411 |  | 1.2904 | -13.8603 | 41.2942 | 596.8284 |  | 1.2954 | -13.9132 | 41.4518 | 599.1067 |  | 1.2989 | -13.951 | 41.5644 | 600.734 |  | 1.3015 | -13.9794 | 41.6489 | 601.9545 |  | 1.3036 | -14.0014 | 41.7146 | 602.9038 |  | 1.3052 | -14.0191 | 41.7671 | 603.6632 |  | 1.3066 | -14.0335 | 41.8101 | 604.2845 |  | 1.3077 | -14.0455 | 41.8459 | 604.8023
at | 3 | 8 | 4 | 32 | 0.22 | 0 | 170 | 13.6653 | 169.4499 | at | -0.11611 | 1.2471 | -0.27437 | -3.8743 | at | -0.0018305 | 0.019661 | -0.0043254 | -0.061079 | at | 0.12195 | -1.3099 | 3.9025 | 55.1061 | at | 0.25647 | -2.7547 | 8.2071 | 115.8917 | at | 0.40319 | -4.3306 | 12.9022 | 182.1896 | at | 0.56385 | -6.0562 | 18.0432 | 254.7855 | at | 0.74053 | -7.9539 | 23.697 | 334.6213 | at | 0.93576 | -10.0507 | 29.9442 | 422.8371 | at | 1.1525 | -12.3783 | 36.8787 | 520.7579 | at | 1.1893 | -12.7742 | 38.0584 | 537.4156 | at | 1.2129 | -13.0274 | 38.8125 | 548.065 | at | 1.2293 | -13.2031 | 39.3362 | 555.46 | at | 1.2413 | -13.3323 | 39.7211 | 560.8947 | at | 1.2505 | -13.4313 | 40.0159 | 565.0573 | at | 1.2578 | -13.5095 | 40.2489 | 568.3477 | at | 1.2637 | -13.5729 | 40.4377 | 571.0141 | at | 1.2686 | -13.6252 | 40.5938 | 573.2185 | at | 1.2788 | -13.7358 | 40.9231 | 577.8675 | at | 1.2857 | -13.8094 | 41.1426 | 580.9668 | at | 1.2906 | -13.862 | 41.2993 | 583.1807 | at | 1.2943 | -13.9015 | 41.4169 | 584.841 | at | 1.2971 | -13.9322 | 41.5084 | 586.1324 | at | 1.2994 | -13.9568 | 41.5815 | 587.1655 | at | 1.3013 | -13.9769 | 41.6414 | 588.0108 | at | 1.3029 | -13.9936 | 41.6913 | 588.7152
| 4 | 8 | 4 | 32 | 0.22 | 0 | 166 | 13.3438 | 165.4628 |  | -0.14883 | 1.5986 | -0.35169 | -4.8493 |  | -0.035859 | 0.38515 | -0.084733 | -1.1683 |  | 0.086509 | -0.92917 | 2.7683 | 38.1708 |  | 0.21949 | -2.3575 | 7.0238 | 96.8478 |  | 0.36454 | -3.9154 | 11.6652 | 160.8459 |  | 0.52336 | -5.6213 | 16.7475 | 230.9235 |  | 0.69802 | -7.4972 | 22.3366 | 307.9899 |  | 0.89101 | -9.5701 | 28.5124 | 393.1456 |  | 1.1052 | -11.8711 | 35.3678 | 487.6715 |  | 1.1525 | -12.3787 | 36.8799 | 508.5213 |  | 1.1827 | -12.7031 | 37.8466 | 521.8506 |  | 1.2037 | -12.9285 | 38.5179 | 531.1067 |  | 1.2191 | -13.094 | 39.0112 | 537.9091 |  | 1.2309 | -13.2209 | 39.3891 | 543.1193 |  | 1.2402 | -13.3211 | 39.6878 | 547.2377 |  | 1.2478 | -13.4024 | 39.9298 | 550.5751 |  | 1.2541 | -13.4695 | 40.1299 | 553.3343 |  | 1.2672 | -13.6112 | 40.5519 | 559.1532 |  | 1.276 | -13.7056 | 40.8333 | 563.0325 |  | 1.2823 | -13.7731 | 41.0342 | 565.8035 |  | 1.287 | -13.8237 | 41.185 | 567.8817 |  | 1.2907 | -13.863 | 41.3022 | 569.4981 |  | 1.2936 | -13.8945 | 41.396 | 570.7912 |  | 1.296 | -13.9202 | 41.4727 | 571.8492 |  | 1.298 | -13.9417 | 41.5366 | 572.7308
| 1 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 159.9 | 12.8534 | 159.3826 |  | -0.19873 | 2.1346 | -0.3209 | -4.2621 |  | -0.087752 | 0.94252 | -0.14169 | -1.8819 |  | 0.032459 | -0.34863 | 2.0295 | 26.9552 |  | 0.1631 | -1.7518 | 10.1977 | 135.4445 |  | 0.30558 | -3.2822 | 19.1067 | 253.7723 |  | 0.46161 | -4.958 | 28.8619 | 383.3404 |  | 0.63319 | -6.8009 | 39.5901 | 525.8304 |  | 0.82278 | -8.8373 | 51.4443 | 683.2768 |  | 1.0332 | -11.0978 | 64.6033 | 858.0537 |  | 1.0963 | -11.7755 | 68.5485 | 910.4524 |  | 1.1367 | -12.2087 | 71.0706 | 943.9509 |  | 1.1647 | -12.5096 | 72.822 | 967.2126 |  | 1.1853 | -12.7307 | 74.1091 | 984.308 |  | 1.201 | -12.9 | 75.0949 | 997.402 |  | 1.2135 | -13.0339 | 75.8742 | 1007.7523 |  | 1.2236 | -13.1424 | 76.5057 | 1016.1395 |  | 1.232 | -13.2321 | 77.0278 | 1023.0738 |  | 1.2496 | -13.4212 | 78.1288 | 1037.6977 |  | 1.2613 | -13.5473 | 78.8629 | 1047.447 |  | 1.2697 | -13.6374 | 79.3872 | 1054.4107 |  | 1.276 | -13.7049 | 79.7804 | 1059.6336 |  | 1.2809 | -13.7575 | 80.0862 | 1063.6958 |  | 1.2848 | -13.7995 | 80.3309 | 1066.9455 |  | 1.288 | -13.8339 | 80.5311 | 1069.6044 |  | 1.2907 | -13.8625 | 80.6979 | 1071.8202
| 2 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 151.7 | 12.1943 | 151.2091 |  | -0.26582 | 2.8551 | -0.42921 | -5.4084 |  | -0.15751 | 1.6918 | -0.25433 | -3.2048 |  | -0.0402 | 0.43177 | -0.06491 | -0.81791 |  | 0.087288 | -0.93754 | 5.4577 | 68.771 |  | 0.22634 | -2.431 | 14.1517 | 178.3224 |  | 0.37859 | -4.0664 | 23.6716 | 298.2805 |  | 0.54604 | -5.8648 | 34.141 | 430.2021 |  | 0.73105 | -7.8521 | 45.7092 | 575.9707 |  | 0.93645 | -10.0581 | 58.5514 | 737.7918 |  | 1.0208 | -10.9646 | 63.8281 | 804.283 |  | 1.0748 | -11.5441 | 67.2016 | 846.7907 |  | 1.1123 | -11.9465 | 69.5441 | 876.3086 |  | 1.1398 | -12.2422 | 71.2657 | 898.0018 |  | 1.1609 | -12.4688 | 72.5843 | 914.6174 |  | 1.1776 | -12.6478 | 73.6266 | 927.7514 |  | 1.1911 | -12.7929 | 74.4713 | 938.3943 |  | 1.2022 | -12.9129 | 75.1696 | 947.1935 |  | 1.2258 | -13.1658 | 76.6423 | 965.7504 |  | 1.2415 | -13.3345 | 77.624 | 978.1217 |  | 1.2527 | -13.455 | 78.3253 | 986.9584 |  | 1.2611 | -13.5453 | 78.8513 | 993.5859 |  | 1.2677 | -13.6156 | 79.2604 | 998.7406 |  | 1.2729 | -13.6718 | 79.5876 | 1002.8644 |  | 1.2772 | -13.7178 | 79.8554 | 1006.2384 |  | 1.2807 | -13.7561 | 80.0785 | 1009.05
| 3 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 143.5 | 11.5351 | 143.0356 |  | -0.3329 | 3.5756 | -0.53752 | -6.4071 |  | -0.22727 | 2.441 | -0.36697 | -4.3741 |  | -0.11286 | 1.2122 | -0.18223 | -2.1721 |  | 0.011478 | -0.12329 | 0.71768 | 8.5545 |  | 0.14709 | -1.5799 | 9.1968 | 109.6224 |  | 0.29558 | -3.1748 | 18.4814 | 220.2911 |  | 0.45889 | -4.9288 | 28.6919 | 341.9968 |  | 0.63933 | -6.8669 | 39.9741 | 476.4772 |  | 0.83966 | -9.0185 | 52.4994 | 625.7742 |  | 0.94535 | -10.1537 | 59.1078 | 704.5438 |  | 1.0129 | -10.8795 | 63.3326 | 754.9011 |  | 1.0598 | -11.3834 | 66.2663 | 789.8699 |  | 1.0943 | -11.7538 | 68.4223 | 815.5689 |  | 1.1207 | -12.0375 | 70.0737 | 835.2529 |  | 1.1416 | -12.2617 | 71.379 | 850.8122 |  | 1.1585 | -12.4434 | 72.4368 | 863.4205 |  | 1.1725 | -12.5937 | 73.3113 | 873.8445 |  | 1.202 | -12.9105 | 75.1557 | 895.8283 |  | 1.2217 | -13.1217 | 76.3852 | 910.4841 |  | 1.2357 | -13.2726 | 77.2635 | 920.9525 |  | 1.2463 | -13.3857 | 77.9222 | 928.8039 |  | 1.2544 | -13.4737 | 78.4345 | 934.9105 |  | 1.261 | -13.5441 | 78.8443 | 939.7958 |  | 1.2664 | -13.6017 | 79.1797 | 943.7928 |  | 1.2708 | -13.6497 | 79.4591 | 947.1237
| 4 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 135.3 | 10.876 | 134.8622 |  | -0.39998 | 4.296 | -0.64584 | -7.2583 |  | -0.29703 | 3.1903 | -0.47961 | -5.3901 |  | -0.18552 | 1.9926 | -0.29955 | -3.3665 |  | -0.064332 | 0.69097 | -0.10388 | -1.1674 |  | 0.067843 | -0.72868 | 4.2419 | 47.6721 |  | 0.21257 | -2.2832 | 13.2911 | 149.372 |  | 0.37174 | -3.9927 | 23.2428 | 261.2144 |  | 0.54761 | -5.8817 | 34.2391 | 384.7963 |  | 0.74286 | -7.9789 | 46.4475 | 522.0008 |  | 0.86985 | -9.3429 | 54.3875 | 611.2348 |  | 0.95104 | -10.2148 | 59.4636 | 668.282 |  | 1.0074 | -10.8204 | 62.9884 | 707.8963 |  | 1.0488 | -11.2654 | 65.5789 | 737.0095 |  | 1.0806 | -11.6062 | 67.5631 | 759.3084 |  | 1.1057 | -11.8756 | 69.1315 | 776.9348 |  | 1.126 | -12.0939 | 70.4024 | 791.218 |  | 1.1428 | -12.2744 | 71.4531 | 803.0269 |  | 1.1782 | -12.6551 | 73.6691 | 827.9312 |  | 1.2019 | -12.9089 | 75.1464 | 844.534 |  | 1.2187 | -13.0902 | 76.2016 | 856.3932 |  | 1.2314 | -13.2261 | 76.9931 | 865.2876 |  | 1.2412 | -13.3319 | 77.6086 | 872.2054 |  | 1.2491 | -13.4164 | 78.101 | 877.7397 |  | 1.2556 | -13.4857 | 78.504 | 882.2677 |  | 1.2609 | -13.5433 | 78.8397 | 886.0411
| 5 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 127.1 | 10.2168 | 126.6887 |  | -0.46706 | 5.0165 | -0.75415 | -7.9619 |  | -0.36678 | 3.9395 | -0.59224 | -6.2525 |  | -0.25817 | 2.773 | -0.41687 | -4.4011 |  | -0.14014 | 1.5052 | -0.22628 | -2.389 |  | -0.011405 | 0.12249 | -0.018415 | -0.19442 |  | 0.12956 | -1.3916 | 8.1008 | 85.5234 |  | 0.28459 | -3.0567 | 17.7937 | 187.8551 |  | 0.45588 | -4.8965 | 28.504 | 300.9279 |  | 0.64607 | -6.9393 | 40.3955 | 426.4716 |  | 0.79436 | -8.532 | 49.6672 | 524.356 |  | 0.88916 | -9.5502 | 55.5946 | 586.9335 |  | 0.95499 | -10.2573 | 59.7106 | 630.388 |  | 1.0034 | -10.7769 | 62.7355 | 662.3235 |  | 1.0404 | -11.1749 | 65.0524 | 686.784 |  | 1.0697 | -11.4895 | 66.8839 | 706.1192 |  | 1.0934 | -11.7445 | 68.3679 | 721.787 |  | 1.1131 | -11.9552 | 69.5949 | 734.7406 |  | 1.1545 | -12.3997 | 72.1825 | 762.0591 |  | 1.182 | -12.6961 | 73.9076 | 780.2715 |  | 1.2018 | -12.9078 | 75.1398 | 793.2803 |  | 1.2165 | -13.0665 | 76.064 | 803.0369 |  | 1.228 | -13.19 | 76.7827 | 810.6254 |  | 1.2372 | -13.2888 | 77.3578 | 816.6962 |  | 1.2448 | -13.3696 | 77.8282 | 821.6632 |  | 1.251 | -13.4369 | 78.2203 | 825.8023
| 6 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 118.9 | 9.5577 | 118.5152 |  | -0.53414 | 5.737 | -0.86247 | -8.518 |  | -0.43654 | 4.6888 | -0.70488 | -6.9616 |  | -0.33083 | 3.5534 | -0.53419 | -5.2758 |  | -0.21595 | 2.3195 | -0.34869 | -3.4438 |  | -0.090652 | 0.97367 | -0.14637 | -1.4456 |  | 0.04655 | -0.49998 | 2.9105 | 28.7452 |  | 0.19743 | -2.1206 | 12.3446 | 121.9187 |  | 0.36416 | -3.9113 | 22.7689 | 224.8721 |  | 0.54928 | -5.8997 | 34.3436 | 339.1866 |  | 0.71886 | -7.7211 | 44.9469 | 443.9075 |  | 0.82728 | -8.8856 | 51.7256 | 510.8555 |  | 0.90256 | -9.6942 | 56.4327 | 557.345 |  | 0.95789 | -10.2885 | 59.8921 | 591.5108 |  | 1.0003 | -10.7436 | 62.5418 | 617.6797 |  | 1.0338 | -11.1034 | 64.6363 | 638.3653 |  | 1.0609 | -11.395 | 66.3335 | 655.1274 |  | 1.0834 | -11.636 | 67.7367 | 668.9857 |  | 1.1307 | -12.1444 | 70.6959 | 698.2122 |  | 1.1622 | -12.4833 | 72.6688 | 717.6965 |  | 1.1848 | -12.7253 | 74.078 | 731.6139 |  | 1.2017 | -12.9069 | 75.1348 | 742.0519 |  | 1.2148 | -13.0481 | 75.9569 | 750.1704 |  | 1.2253 | -13.1611 | 76.6145 | 756.6652 |  | 1.2339 | -13.2535 | 77.1525 | 761.9791 |  | 1.2411 | -13.3305 | 77.6009 | 766.4073
| 7 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 110.7 | 8.8985 | 110.3418 |  | -0.60122 | 6.4575 | -0.97078 | -8.9265 |  | -0.5063 | 5.438 | -0.81752 | -7.5172 |  | -0.40349 | 4.3338 | -0.65151 | -5.9908 |  | -0.29176 | 3.1337 | -0.4711 | -4.3319 |  | -0.1699 | 1.8248 | -0.27433 | -2.5225 |  | -0.036461 | 0.39162 | -0.058874 | -0.54135 |  | 0.11028 | -1.1845 | 6.8955 | 63.4053 |  | 0.27243 | -2.9261 | 17.0339 | 156.6289 |  | 0.45249 | -4.86 | 28.2916 | 260.1459 |  | 0.64337 | -6.9102 | 40.2266 | 369.8892 |  | 0.7654 | -8.2209 | 47.8565 | 440.048 |  | 0.85014 | -9.1311 | 53.1549 | 488.7671 |  | 0.91241 | -9.8 | 57.0487 | 524.5716 |  | 0.96011 | -10.3123 | 60.0312 | 551.9956 |  | 0.99782 | -10.7173 | 62.3887 | 573.6732 |  | 1.0284 | -11.0455 | 64.299 | 591.2392 |  | 1.0536 | -11.3168 | 65.8785 | 605.7622 |  | 1.1069 | -11.889 | 69.2094 | 636.3903 |  | 1.1424 | -12.2705 | 71.43 | 656.8091 |  | 1.1678 | -12.5429 | 73.0161 | 671.394 |  | 1.1868 | -12.7473 | 74.2057 | 682.3326 |  | 1.2016 | -12.9062 | 75.131 | 690.8405 |  | 1.2135 | -13.0334 | 75.8712 | 697.6467 |  | 1.2231 | -13.1374 | 76.4768 | 703.2155 |  | 1.2312 | -13.2241 | 76.9815 | 707.8561
| 8 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 102.5 | 8.2394 | 102.1683 |  | -0.6683 | 7.178 | -1.0791 | -9.1875 |  | -0.57606 | 6.1873 | -0.93016 | -7.9194 |  | -0.47615 | 5.1142 | -0.76883 | -6.5459 |  | -0.36757 | 3.948 | -0.59351 | -5.0532 |  | -0.24915 | 2.676 | -0.40229 | -3.4251 |  | -0.11947 | 1.2832 | -0.19291 | -1.6425 |  | 0.023134 | -0.24847 | 1.4464 | 12.3149 |  | 0.18071 | -1.9409 | 11.2988 | 96.1982 |  | 0.35569 | -3.8204 | 22.2397 | 189.3494 |  | 0.56787 | -6.0994 | 35.5062 | 302.3011 |  | 0.70352 | -7.5563 | 43.9875 | 374.511 |  | 0.79771 | -8.568 | 49.8771 | 424.6545 |  | 0.86694 | -9.3116 | 54.2053 | 461.5057 |  | 0.91996 | -9.8811 | 57.5206 | 489.7314 |  | 0.96187 | -10.3312 | 60.1411 | 512.0428 |  | 0.99584 | -10.696 | 62.2646 | 530.1224 |  | 1.0239 | -10.9976 | 64.0202 | 545.0699 |  | 1.0831 | -11.6336 | 67.7228 | 576.5936 |  | 1.1226 | -12.0577 | 70.1912 | 597.6093 |  | 1.1508 | -12.3605 | 71.9543 | 612.6206 |  | 1.172 | -12.5877 | 73.2766 | 623.879 |  | 1.1884 | -12.7644 | 74.3051 | 632.6356 |  | 1.2016 | -12.9057 | 75.1279 | 639.6408 |  | 1.2123 | -13.0213 | 75.8011 | 645.3724 |  | 1.2213 | -13.1177 | 76.3621 | 650.1487
| 9 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 94.3 | 7.5802 | 93.9948 |  | -0.73538 | 7.8985 | -1.1874 | -9.3009 |  | -0.64582 | 6.9366 | -1.0428 | -8.1681 |  | -0.54881 | 5.8946 | -0.88615 | -6.9412 |  | -0.44338 | 4.7622 | -0.71592 | -5.6078 |  | -0.32839 | 3.5272 | -0.53025 | -4.1534 |  | -0.20248 | 2.1748 | -0.32695 | -2.561 |  | -0.064017 | 0.68759 | -0.10337 | -0.80967 |  | 0.088984 | -0.95575 | 5.5637 | 43.5801 |  | 0.2589 | -2.7808 | 16.1878 | 126.7971 |  | 0.49238 | -5.2885 | 30.7859 | 241.1432 |  | 0.64164 | -6.8917 | 40.1185 | 314.2446 |  | 0.74529 | -8.005 | 46.5992 | 365.0071 |  | 0.82146 | -8.8231 | 51.362 | 402.3132 |  | 0.87981 | -9.4498 | 55.0099 | 430.8874 |  | 0.92593 | -9.9451 | 57.8935 | 453.4742 |  | 0.9633 | -10.3465 | 60.2302 | 471.777 |  | 0.99419 | -10.6784 | 62.162 | 486.9091 |  | 1.0594 | -11.3783 | 66.2362 | 518.8219 |  | 1.1028 | -11.8449 | 68.9523 | 540.0971 |  | 1.1338 | -12.1781 | 70.8924 | 555.2936 |  | 1.1571 | -12.4281 | 72.3475 | 566.6911 |  | 1.1752 | -12.6225 | 73.4792 | 575.5557 |  | 1.1897 | -12.778 | 74.3846 | 582.6474 |  | 1.2015 | -12.9053 | 75.1254 | 588.4498 |  | 1.2114 | -13.0113 | 75.7427 | 593.285
wt | 10 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 86.1 | 6.9211 | 85.8214 | wt | -0.80246 | 8.619 | -1.2957 | -9.2668 | wt | -0.71557 | 7.6858 | -1.1554 | -8.2634 | wt | -0.62146 | 6.675 | -1.0035 | -7.1766 | wt | -0.51919 | 5.5765 | -0.83833 | -5.9956 | wt | -0.40764 | 4.3784 | -0.65821 | -4.7074 | wt | -0.2855 | 3.0664 | -0.46099 | -3.2969 | wt | -0.15117 | 1.6237 | -0.24409 | -1.7457 | wt | -0.0027405 | 0.029435 | -0.0044251 | -0.031647 | wt | 0.16211 | -1.7412 | 10.1358 | 72.4891 | wt | 0.41688 | -4.4776 | 26.0656 | 186.4156 | wt | 0.57976 | -6.2271 | 36.2495 | 259.2487 | wt | 0.69286 | -7.4419 | 43.3214 | 309.8249 | wt | 0.77599 | -8.3347 | 48.5186 | 346.9942 | wt | 0.83965 | -9.0185 | 52.4993 | 375.4635 | wt | 0.88998 | -9.559 | 55.6459 | 397.9674 | wt | 0.93076 | -9.997 | 58.1957 | 416.2031 | wt | 0.96447 | -10.3592 | 60.3038 | 431.2796 | wt | 1.0356 | -11.1229 | 64.7496 | 463.0753 | wt | 1.083 | -11.632 | 67.7135 | 484.2724 | wt | 1.1168 | -11.9957 | 69.8306 | 499.4132 | wt | 1.1422 | -12.2685 | 71.4184 | 510.7688 | wt | 1.162 | -12.4806 | 72.6534 | 519.6009 | wt | 1.1778 | -12.6503 | 73.6413 | 526.6666 | wt | 1.1907 | -12.7892 | 74.4497 | 532.4476 | wt | 1.2015 | -12.9049 | 75.1233 | 537.2652
| 11 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 77.9 | 6.2619 | 77.6479 |  | -0.86954 | 9.3395 | -1.404 | -9.0851 |  | -0.78533 | 8.4351 | -1.2681 | -8.2053 |  | -0.69412 | 7.4554 | -1.1208 | -7.2523 |  | -0.595 | 6.3907 | -0.96074 | -6.2166 |  | -0.48689 | 5.2295 | -0.78617 | -5.0871 |  | -0.36851 | 3.958 | -0.59502 | -3.8502 |  | -0.23832 | 2.5597 | -0.38481 | -2.49 |  | -0.094465 | 1.0146 | -0.15253 | -0.98698 |  | 0.065316 | -0.70154 | 4.0839 | 26.4253 |  | 0.34139 | -3.6668 | 21.3453 | 138.1182 |  | 0.51788 | -5.5624 | 32.3805 | 209.5233 |  | 0.64044 | -6.8788 | 40.0435 | 259.108 |  | 0.73051 | -7.8462 | 45.6752 | 295.5485 |  | 0.7995 | -8.5872 | 49.9887 | 323.4597 |  | 0.85403 | -9.1729 | 53.3983 | 345.5224 |  | 0.89822 | -9.6476 | 56.1613 | 363.4005 |  | 0.93476 | -10.04 | 58.4456 | 378.1814 |  | 1.0118 | -10.8675 | 63.2631 | 409.3537 |  | 1.0632 | -11.4192 | 66.4747 | 430.1353 |  | 1.0999 | -11.8133 | 68.7688 | 444.9792 |  | 1.1274 | -12.1089 | 70.4893 | 456.1122 |  | 1.1488 | -12.3387 | 71.8275 | 464.7711 |  | 1.1659 | -12.5227 | 72.898 | 471.6983 |  | 1.1799 | -12.6731 | 73.7739 | 477.366 |  | 1.1916 | -12.7985 | 74.5039 | 482.0891
| 12 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 69.7 | 5.6028 | 69.4744 |  | -0.93662 | 10.06 | -1.5124 | -8.7558 |  | -0.85509 | 9.1843 | -1.3807 | -7.9937 |  | -0.76678 | 8.2358 | -1.2381 | -7.1681 |  | -0.67081 | 7.205 | -1.0832 | -6.2709 |  | -0.56614 | 6.0807 | -0.91413 | -5.2924 |  | -0.45152 | 4.8496 | -0.72906 | -4.2209 |  | -0.32547 | 3.4958 | -0.52553 | -3.0426 |  | -0.18619 | 1.9998 | -0.30064 | -1.7406 |  | -0.031477 | 0.33808 | -0.050825 | -0.29426 |  | 0.26589 | -2.8559 | 16.625 | 96.251 |  | 0.456 | -4.8978 | 28.5115 | 165.0685 |  | 0.58802 | -6.3157 | 36.7657 | 212.8562 |  | 0.68503 | -7.3578 | 42.8318 | 247.9762 |  | 0.75934 | -8.1559 | 47.478 | 274.8759 |  | 0.81808 | -8.7868 | 51.1507 | 296.1391 |  | 0.86568 | -9.2981 | 54.1268 | 313.3693 |  | 0.90504 | -9.7208 | 56.5874 | 327.6146 |  | 0.98803 | -10.6122 | 61.7765 | 357.6573 |  | 1.0434 | -11.2064 | 65.2359 | 377.6857 |  | 1.0829 | -11.6309 | 67.7069 | 391.9917 |  | 1.1125 | -11.9493 | 69.5602 | 402.7212 |  | 1.1356 | -12.1969 | 71.0016 | 411.0664 |  | 1.154 | -12.395 | 72.1547 | 417.7426 |  | 1.1691 | -12.557 | 73.0982 | 423.2049 |  | 1.1817 | -12.6921 | 73.8845 | 427.7568
| 13 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 61.5 | 4.9436 | 61.301 |  | -1.0037 | 10.7805 | -1.6207 | -8.2791 |  | -0.92485 | 9.9336 | -1.4933 | -7.6286 |  | -0.83944 | 9.0162 | -1.3554 | -6.9241 |  | -0.74662 | 8.0192 | -1.2056 | -6.1585 |  | -0.64538 | 6.9319 | -1.0421 | -5.3234 |  | -0.53453 | 5.7412 | -0.8631 | -4.4091 |  | -0.41262 | 4.4318 | -0.66625 | -3.4035 |  | -0.27791 | 2.985 | -0.44875 | -2.2924 |  | -0.12827 | 1.3777 | -0.20712 | -1.058 |  | 0.1904 | -2.045 | 11.9047 | 60.814 |  | 0.39412 | -4.2332 | 24.6425 | 125.8842 |  | 0.53559 | -5.7526 | 33.4878 | 171.0697 |  | 0.63956 | -6.8693 | 39.9884 | 204.2773 |  | 0.71919 | -7.7246 | 44.9674 | 229.7122 |  | 0.78214 | -8.4007 | 48.9031 | 249.8176 |  | 0.83314 | -8.9486 | 52.0924 | 266.1096 |  | 0.87532 | -9.4015 | 54.7291 | 279.5792 |  | 0.96425 | -10.3568 | 60.2899 | 307.9859 |  | 1.0235 | -10.9936 | 63.9971 | 326.9237 |  | 1.0659 | -11.4485 | 66.6451 | 340.4507 |  | 1.0977 | -11.7897 | 68.6311 | 350.596 |  | 1.1224 | -12.055 | 70.1757 | 358.4868 |  | 1.1421 | -12.2673 | 71.4115 | 364.7994 |  | 1.1583 | -12.441 | 72.4225 | 369.9642 |  | 1.1718 | -12.5857 | 73.265 | 374.2683
| 14 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 53.3 | 4.2845 | 53.1275 |  | -1.0708 | 11.501 | -1.729 | -7.6547 |  | -0.99461 | 10.6828 | -1.606 | -7.1102 |  | -0.9121 | 9.7966 | -1.4728 | -6.5203 |  | -0.82243 | 8.8335 | -1.328 | -5.8793 |  | -0.72463 | 7.7831 | -1.1701 | -5.1802 |  | -0.61754 | 6.6328 | -0.99714 | -4.4146 |  | -0.49977 | 5.3679 | -0.80697 | -3.5727 |  | -0.36964 | 3.9702 | -0.59685 | -2.6424 |  | -0.22506 | 2.4173 | -0.36341 | -1.6089 |  | 0.1149 | -1.2342 | 7.1844 | 31.8072 |  | 0.33224 | -3.5685 | 20.7735 | 91.9704 |  | 0.48317 | -5.1896 | 30.21 | 133.7485 |  | 0.59408 | -6.3809 | 37.145 | 164.4518 |  | 0.67904 | -7.2934 | 42.4568 | 187.9686 |  | 0.74619 | -8.0146 | 46.6556 | 206.5578 |  | 0.80061 | -8.5991 | 50.0579 | 221.6212 |  | 0.8456 | -9.0823 | 52.8709 | 234.075 |  | 0.94048 | -10.1014 | 58.8033 | 260.3396 |  | 1.0037 | -10.7808 | 62.7583 | 277.8493 |  | 1.0489 | -11.2661 | 65.5832 | 290.3562 |  | 1.0828 | -11.6301 | 67.702 | 299.7364 |  | 1.1092 | -11.9131 | 69.3499 | 307.0321 |  | 1.1302 | -12.1396 | 70.6682 | 312.8687 |  | 1.1475 | -12.3249 | 71.7468 | 317.6441 |  | 1.1619 | -12.4793 | 72.6456 | 321.6235
| 15 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 45.1 | 3.6253 | 44.9541 |  | -1.1379 | 12.2215 | -1.8373 | -6.8828 |  | -1.0644 | 11.4321 | -1.7186 | -6.4383 |  | -0.98476 | 10.577 | -1.5901 | -5.9567 |  | -0.89824 | 9.6478 | -1.4504 | -5.4334 |  | -0.80388 | 8.6342 | -1.298 | -4.8626 |  | -0.70055 | 7.5244 | -1.1312 | -4.2376 |  | -0.58692 | 6.304 | -0.9477 | -3.5502 |  | -0.46136 | 4.9554 | -0.74496 | -2.7907 |  | -0.32185 | 3.457 | -0.5197 | -1.9469 |  | 0.039409 | -0.42328 | 2.464 | 9.2307 |  | 0.27036 | -2.9039 | 16.9045 | 63.3272 |  | 0.43074 | -4.6265 | 26.9321 | 100.8924 |  | 0.54861 | -5.8924 | 34.3016 | 128.4997 |  | 0.63888 | -6.8621 | 39.9462 | 149.6452 |  | 0.71024 | -7.6285 | 44.408 | 166.3598 |  | 0.76807 | -8.2496 | 48.0235 | 179.9043 |  | 0.81588 | -8.7631 | 51.0127 | 191.1023 |  | 0.9167 | -9.8461 | 57.3168 | 214.7184 |  | 0.98392 | -10.568 | 61.5195 | 230.4624 |  | 1.0319 | -11.0837 | 64.5214 | 241.7082 |  | 1.0679 | -11.4704 | 66.7728 | 250.1425 |  | 1.0959 | -11.7713 | 68.524 | 256.7025 |  | 1.1184 | -12.0119 | 69.9249 | 261.9506 |  | 1.1367 | -12.2088 | 71.0711 | 266.2444 |  | 1.152 | -12.3729 | 72.0262 | 269.8226
| 16 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 36.9 | 2.9662 | 36.7806 |  | -1.2049 | 12.942 | -1.9456 | -5.9634 |  | -1.1341 | 12.1813 | -1.8313 | -5.6129 |  | -1.0574 | 11.3574 | -1.7074 | -5.2333 |  | -0.97405 | 10.462 | -1.5728 | -4.8207 |  | -0.88312 | 9.4854 | -1.426 | -4.3707 |  | -0.78356 | 8.416 | -1.2652 | -3.8779 |  | -0.67407 | 7.24 | -1.0884 | -3.3361 |  | -0.55309 | 5.9406 | -0.89306 | -2.7373 |  | -0.41865 | 4.4966 | -0.67598 | -2.0719 |  | -0.036086 | 0.38759 | -0.058268 | -0.17859 |  | 0.20848 | -2.2393 | 13.0355 | 39.9544 |  | 0.37832 | -4.0634 | 23.6543 | 72.5016 |  | 0.50313 | -5.404 | 31.4582 | 96.421 |  | 0.59873 | -6.4308 | 37.4355 | 114.7417 |  | 0.6743 | -7.2424 | 42.1604 | 129.2236 |  | 0.73553 | -7.9001 | 45.9891 | 140.9587 |  | 0.78616 | -8.4439 | 49.1545 | 150.6609 |  | 0.89293 | -9.5907 | 55.8302 | 171.1222 |  | 0.9641 | -10.3552 | 60.2806 | 184.7632 |  | 1.0149 | -10.9013 | 63.4596 | 194.5067 |  | 1.0531 | -11.3108 | 65.8437 | 201.8143 |  | 1.0827 | -11.6294 | 67.6981 | 207.498 |  | 1.1065 | -11.8842 | 69.1816 | 212.045 |  | 1.1259 | -12.0927 | 70.3954 | 215.7652 |  | 1.1421 | -12.2665 | 71.4068 | 218.8654
| 17 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 28.7 | 2.307 | 28.6071 |  | -1.272 | 13.6625 | -2.0539 | -4.8964 |  | -1.2039 | 12.9306 | -1.9439 | -4.6341 |  | -1.1301 | 12.1378 | -1.8247 | -4.35 |  | -1.0499 | 11.2763 | -1.6952 | -4.0412 |  | -0.96237 | 10.3366 | -1.5539 | -3.7045 |  | -0.86657 | 9.3076 | -1.3992 | -3.3357 |  | -0.76122 | 8.1761 | -1.2291 | -2.9302 |  | -0.64481 | 6.9258 | -1.0412 | -2.4821 |  | -0.51544 | 5.5362 | -0.83227 | -1.9841 |  | -0.11158 | 1.1985 | -0.18017 | -0.42951 |  | 0.14661 | -1.5746 | 9.1665 | 21.8522 |  | 0.32589 | -3.5003 | 20.3764 | 48.576 |  | 0.45765 | -4.9155 | 28.6148 | 68.2156 |  | 0.55858 | -5.9995 | 34.9249 | 83.2584 |  | 0.63835 | -6.8563 | 39.9128 | 95.1492 |  | 0.70299 | -7.5507 | 43.9546 | 104.7846 |  | 0.75644 | -8.1247 | 47.2963 | 112.7508 |  | 0.86915 | -9.3353 | 54.3436 | 129.5512 |  | 0.94429 | -10.1424 | 59.0418 | 140.7514 |  | 0.99796 | -10.7189 | 62.3977 | 148.7516 |  | 1.0382 | -11.1512 | 64.9146 | 154.7517 |  | 1.0695 | -11.4875 | 66.8722 | 159.4185 |  | 1.0946 | -11.7565 | 68.4383 | 163.1519 |  | 1.1151 | -11.9767 | 69.7196 | 166.2065 |  | 1.1321 | -12.1601 | 70.7874 | 168.752
| 18 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 20.5 | 1.6479 | 20.4337 |  | -1.3391 | 14.383 | -2.1622 | -3.6819 |  | -1.2736 | 13.6798 | -2.0565 | -3.5019 |  | -1.2027 | 12.9182 | -1.942 | -3.3069 |  | -1.1257 | 12.0905 | -1.8176 | -3.095 |  | -1.0416 | 11.1878 | -1.6819 | -2.8639 |  | -0.94958 | 10.1992 | -1.5333 | -2.6109 |  | -0.84837 | 9.1121 | -1.3699 | -2.3326 |  | -0.73654 | 7.9109 | -1.1893 | -2.0251 |  | -0.61223 | 6.5758 | -0.98856 | -1.6833 |  | -0.18708 | 2.0093 | -0.30207 | -0.51437 |  | 0.084726 | -0.91002 | 5.2975 | 9.0206 |  | 0.27347 | -2.9373 | 17.0986 | 29.1156 |  | 0.41218 | -4.4271 | 25.7714 | 43.8837 |  | 0.51842 | -5.5682 | 32.4143 | 55.1952 |  | 0.6024 | -6.4702 | 37.6652 | 64.1365 |  | 0.67045 | -7.2012 | 41.9202 | 71.3819 |  | 0.72672 | -7.8055 | 45.438 | 77.3721 |  | 0.84537 | -9.0799 | 52.857 | 90.0052 |  | 0.92448 | -9.9296 | 57.803 | 98.4273 |  | 0.98098 | -10.5365 | 61.3359 | 104.443 |  | 1.0234 | -10.9916 | 63.9855 | 108.9549 |  | 1.0563 | -11.3456 | 66.0463 | 112.4641 |  | 1.0827 | -11.6289 | 67.695 | 115.2714 |  | 1.1043 | -11.8606 | 69.0439 | 117.5683 |  | 1.1222 | -12.0537 | 70.168 | 119.4824
| 19 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 12.3 | 0.98873 | 12.2602 |  | -1.4062 | 15.1035 | -2.2706 | -2.3198 |  | -1.3434 | 14.4291 | -2.1692 | -2.2162 |  | -1.2754 | 13.6986 | -2.0594 | -2.104 |  | -1.2015 | 12.9048 | -1.94 | -1.9821 |  | -1.1209 | 12.0389 | -1.8099 | -1.8491 |  | -1.0326 | 11.0908 | -1.6673 | -1.7035 |  | -0.93552 | 10.0482 | -1.5106 | -1.5433 |  | -0.82826 | 8.8961 | -1.3374 | -1.3664 |  | -0.70902 | 7.6154 | -1.1449 | -1.1697 |  | -0.26257 | 2.8202 | -0.42397 | -0.43316 |  | 0.022847 | -0.24539 | 1.4285 | 1.4595 |  | 0.22104 | -2.3742 | 13.8208 | 14.1204 |  | 0.3667 | -3.9387 | 22.928 | 23.4252 |  | 0.47827 | -5.1369 | 29.9037 | 30.5521 |  | 0.56646 | -6.0841 | 35.4176 | 36.1856 |  | 0.63792 | -6.8517 | 39.8857 | 40.7506 |  | 0.697 | -7.4863 | 43.5798 | 44.5248 |  | 0.8216 | -8.8246 | 51.3705 | 52.4843 |  | 0.90467 | -9.7168 | 56.5642 | 57.7907 |  | 0.964 | -10.3541 | 60.274 | 61.581 |  | 1.0085 | -10.832 | 63.0564 | 64.4237 |  | 1.0431 | -11.2038 | 65.2205 | 66.6347 |  | 1.0708 | -11.5012 | 66.9517 | 68.4034 |  | 1.0935 | -11.7445 | 68.3682 | 69.8506 |  | 1.1123 | -11.9473 | 69.5486 | 71.0566
| 20 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 4.1 | 0.32958 | 4.0867 |  | -1.4733 | 15.824 | -2.3789 | -0.81015 |  | -1.4132 | 15.1783 | -2.2818 | -0.7771 |  | -1.348 | 14.479 | -2.1767 | -0.74129 |  | -1.2773 | 13.719 | -2.0624 | -0.70238 |  | -1.2001 | 12.8901 | -1.9378 | -0.65994 |  | -1.1156 | 11.9824 | -1.8014 | -0.61347 |  | -1.0227 | 10.9843 | -1.6513 | -0.56237 |  | -0.91998 | 9.8813 | -1.4855 | -0.5059 |  | -0.80582 | 8.6551 | -1.3011 | -0.44312 |  | -0.33807 | 3.6311 | -0.54587 | -0.1859 |  | -0.039033 | 0.41924 | -0.063026 | -0.021464 |  | 0.16862 | -1.8111 | 10.5429 | 3.5905 |  | 0.32123 | -3.4502 | 20.0846 | 6.84 |  | 0.43811 | -4.7057 | 27.393 | 9.329 |  | 0.53051 | -5.698 | 33.17 | 11.2964 |  | 0.60538 | -6.5022 | 37.8513 | 12.8907 |  | 0.66728 | -7.1671 | 41.7216 | 14.2087 |  | 0.79782 | -8.5692 | 49.8839 | 16.9885 |  | 0.88485 | -9.504 | 55.3254 | 18.8417 |  | 0.94702 | -10.1717 | 59.2122 | 20.1654 |  | 0.99364 | -10.6724 | 62.1273 | 21.1581 |  | 1.0299 | -11.0619 | 64.3946 | 21.9303 |  | 1.0589 | -11.3735 | 66.2084 | 22.548 |  | 1.0826 | -11.6284 | 67.6925 | 23.0534 |  | 1.1024 | -11.8409 | 68.9292 | 23.4746
| 1 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -4.1 | -0.32958 | -4.0867 |  | -1.5403 | 16.5445 | -2.4872 | 0.84704 |  | -1.4829 | 15.9276 | -2.3944 | 0.81546 |  | -1.4207 | 15.2594 | -2.294 | 0.78125 |  | -1.3531 | 14.5333 | -2.1848 | 0.74407 |  | -1.2794 | 13.7413 | -2.0658 | 0.70352 |  | -1.1986 | 12.8741 | -1.9354 | 0.65912 |  | -1.1098 | 11.9203 | -1.792 | 0.61029 |  | -1.0117 | 10.8665 | -1.6336 | 0.55634 |  | -0.90261 | 9.6947 | -1.4574 | 0.49635 |  | -0.41356 | 4.4419 | -0.66777 | 0.22742 |  | -0.10091 | 1.0839 | -0.16294 | 0.055492 |  | 0.11619 | -1.248 | 7.2651 | -2.4742 |  | 0.27575 | -2.9618 | 17.2413 | -5.8717 |  | 0.39796 | -4.2744 | 24.8824 | -8.474 |  | 0.49456 | -5.312 | 30.9224 | -10.531 |  | 0.57284 | -6.1527 | 35.8168 | -12.1978 |  | 0.63756 | -6.8479 | 39.8634 | -13.5759 |  | 0.77405 | -8.3138 | 48.3973 | -16.4822 |  | 0.86504 | -9.2912 | 54.0866 | -18.4198 |  | 0.93003 | -9.9893 | 58.1504 | -19.8037 |  | 0.97878 | -10.5128 | 61.1982 | -20.8417 |  | 1.0167 | -10.92 | 63.5687 | -21.649 |  | 1.047 | -11.2458 | 65.4651 | -22.2949 |  | 1.0718 | -11.5124 | 67.0168 | -22.8233 |  | 1.0925 | -11.7345 | 68.3098 | -23.2637
| 2 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -12.3 | -0.98873 | -12.2602 |  | -1.6074 | 17.265 | -2.5955 | 2.6518 |  | -1.5527 | 16.6768 | -2.5071 | 2.5614 |  | -1.4934 | 16.0398 | -2.4113 | 2.4636 |  | -1.4289 | 15.3475 | -2.3072 | 2.3573 |  | -1.3586 | 14.5925 | -2.1937 | 2.2413 |  | -1.2816 | 13.7657 | -2.0694 | 2.1143 |  | -1.197 | 12.8564 | -1.9327 | 1.9747 |  | -1.1034 | 11.8517 | -1.7817 | 1.8203 |  | -0.9994 | 10.7343 | -1.6137 | 1.6487 |  | -0.48906 | 5.2528 | -0.78967 | 0.8068 |  | -0.16279 | 1.7485 | -0.26286 | 0.26856 |  | 0.06377 | -0.68494 | 3.9872 | -4.0737 |  | 0.23027 | -2.4733 | 14.3979 | -14.7101 |  | 0.35781 | -3.8431 | 22.3718 | -22.8569 |  | 0.45861 | -4.9259 | 28.6748 | -29.2966 |  | 0.5403 | -5.8032 | 33.7824 | -34.5149 |  | 0.60784 | -6.5286 | 38.0052 | -38.8292 |  | 0.75027 | -8.0585 | 46.9107 | -47.9279 |  | 0.84523 | -9.0784 | 52.8478 | -53.9937 |  | 0.91305 | -9.8068 | 57.0885 | -58.3264 |  | 0.96392 | -10.3532 | 60.2691 | -61.5759 |  | 1.0035 | -10.7782 | 62.7428 | -64.1033 |  | 1.0351 | -11.1181 | 64.7219 | -66.1252 |  | 1.061 | -11.3963 | 66.3411 | -67.7795 |  | 1.0826 | -11.6281 | 67.6904 | -69.1581
| 3 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -20.5 | -1.6479 | -20.4337 |  | -1.6745 | 17.9855 | -2.7038 | 4.6041 |  | -1.6224 | 17.4261 | -2.6197 | 4.4609 |  | -1.566 | 16.8202 | -2.5286 | 4.3058 |  | -1.5047 | 16.1618 | -2.4297 | 4.1372 |  | -1.4379 | 15.4436 | -2.3217 | 3.9534 |  | -1.3646 | 14.6573 | -2.2035 | 3.7521 |  | -1.2841 | 13.7925 | -2.0735 | 3.5307 |  | -1.1952 | 12.8369 | -1.9298 | 3.2861 |  | -1.0962 | 11.7739 | -1.77 | 3.014 |  | -0.56455 | 6.0637 | -0.91157 | 1.5522 |  | -0.22467 | 2.4131 | -0.36277 | 0.61773 |  | 0.011346 | -0.12186 | 0.70938 | -1.2079 |  | 0.1848 | -1.9849 | 11.5545 | -19.675 |  | 0.31765 | -3.4118 | 19.8611 | -33.8197 |  | 0.42267 | -4.5398 | 26.4272 | -45.0004 |  | 0.50776 | -5.4538 | 31.748 | -54.0606 |  | 0.57812 | -6.2094 | 36.1469 | -61.5512 |  | 0.7265 | -7.8031 | 45.4241 | -77.3485 |  | 0.82541 | -8.8655 | 51.609 | -87.88 |  | 0.89607 | -9.6244 | 56.0267 | -95.4025 |  | 0.94906 | -10.1936 | 59.34 | -101.0444 |  | 0.99028 | -10.6363 | 61.917 | -105.4325 |  | 1.0232 | -10.9904 | 63.9786 | -108.943 |  | 1.0502 | -11.2802 | 65.6653 | -111.8153 |  | 1.0727 | -11.5217 | 67.071 | -114.2088
| 4 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -28.7 | -2.307 | -28.6071 |  | -1.7416 | 18.706 | -2.8121 | 6.7039 |  | -1.6922 | 18.1754 | -2.7324 | 6.5138 |  | -1.6387 | 17.6006 | -2.646 | 6.3078 |  | -1.5805 | 16.976 | -2.5521 | 6.0839 |  | -1.5171 | 16.2948 | -2.4497 | 5.8398 |  | -1.4477 | 15.5489 | -2.3375 | 5.5725 |  | -1.3713 | 14.7285 | -2.2142 | 5.2785 |  | -1.2869 | 13.8221 | -2.0779 | 4.9536 |  | -1.193 | 12.8136 | -1.9263 | 4.5922 |  | -0.64004 | 6.8746 | -1.0335 | 2.4637 |  | -0.28655 | 3.0778 | -0.46269 | 1.103 |  | -0.041079 | 0.44122 | -0.06633 | 0.15813 |  | 0.13932 | -1.4964 | 8.7111 | -20.7666 |  | 0.2775 | -2.9805 | 17.3505 | -41.3624 |  | 0.38672 | -4.1537 | 24.1796 | -57.6425 |  | 0.47523 | -5.1043 | 29.7135 | -70.8349 |  | 0.5484 | -5.8902 | 34.2887 | -81.7418 |  | 0.70272 | -7.5477 | 43.9376 | -104.744 |  | 0.8056 | -8.6527 | 50.3701 | -120.0787 |  | 0.87909 | -9.442 | 54.9648 | -131.0322 |  | 0.9342 | -10.034 | 58.4109 | -139.2472 |  | 0.97707 | -10.4944 | 61.0911 | -145.6367 |  | 1.0114 | -10.8628 | 63.2353 | -150.7483 |  | 1.0394 | -11.1641 | 64.9896 | -154.9305 |  | 1.0628 | -11.4153 | 66.4516 | -158.4157
| 5 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -36.9 | -2.9662 | -36.7806 |  | -1.8087 | 19.4265 | -2.9204 | 8.9513 |  | -1.7619 | 18.9246 | -2.845 | 8.7201 |  | -1.7113 | 18.381 | -2.7633 | 8.4696 |  | -1.6563 | 17.7903 | -2.6745 | 8.1974 |  | -1.5963 | 17.146 | -2.5776 | 7.9005 |  | -1.5307 | 16.4405 | -2.4715 | 7.5754 |  | -1.4584 | 15.6646 | -2.3549 | 7.2179 |  | -1.3786 | 14.8073 | -2.226 | 6.8229 |  | -1.2898 | 13.8532 | -2.0826 | 6.3833 |  | -0.71554 | 7.6854 | -1.1554 | 3.5413 |  | -0.34843 | 3.7424 | -0.56261 | 1.7244 |  | -0.093504 | 1.0043 | -0.15098 | 0.46276 |  | 0.093845 | -1.008 | 5.8677 | -17.9847 |  | 0.23734 | -2.5492 | 14.8399 | -45.485 |  | 0.35077 | -3.7676 | 21.9321 | -67.2228 |  | 0.44269 | -4.7548 | 27.6791 | -84.8377 |  | 0.51868 | -5.571 | 32.4305 | -99.401 |  | 0.67894 | -7.2924 | 42.451 | -130.1144 |  | 0.78579 | -8.4399 | 49.1313 | -150.5899 |  | 0.8621 | -9.2596 | 53.903 | -165.2153 |  | 0.91934 | -9.8744 | 57.4817 | -176.1844 |  | 0.96386 | -10.3525 | 60.2652 | -184.7159 |  | 0.99947 | -10.7351 | 62.492 | -191.541 |  | 1.0286 | -11.048 | 64.3139 | -197.1253 |  | 1.0529 | -11.3089 | 65.8322 | -201.7788
| 6 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -45.1 | -3.6253 | -44.9541 |  | -1.8758 | 20.147 | -3.0288 | 11.3463 |  | -1.8317 | 19.6739 | -2.9576 | 11.0798 |  | -1.784 | 19.1614 | -2.8806 | 10.7912 |  | -1.7321 | 18.6045 | -2.7969 | 10.4776 |  | -1.6756 | 17.9971 | -2.7056 | 10.1355 |  | -1.6137 | 17.3321 | -2.6056 | 9.761 |  | -1.5456 | 16.6006 | -2.4956 | 9.3491 |  | -1.4703 | 15.7924 | -2.3741 | 8.8939 |  | -1.3866 | 14.8928 | -2.2389 | 8.3872 |  | -0.79103 | 8.4963 | -1.2773 | 4.7849 |  | -0.41031 | 4.407 | -0.66252 | 2.4819 |  | -0.14593 | 1.5674 | -0.23563 | 0.88271 |  | 0.048369 | -0.51952 | 3.0243 | -11.3295 |  | 0.19719 | -2.118 | 12.3293 | -46.1875 |  | 0.31483 | -3.3815 | 19.6845 | -73.7414 |  | 0.41015 | -4.4053 | 25.6446 | -96.0692 |  | 0.48896 | -5.2518 | 30.5723 | -114.529 |  | 0.65517 | -7.037 | 40.9644 | -153.4597 |  | 0.76597 | -8.2271 | 47.8925 | -179.4136 |  | 0.84512 | -9.0772 | 52.8412 | -197.952 |  | 0.90448 | -9.7148 | 56.5526 | -211.8558 |  | 0.95065 | -10.2107 | 59.4393 | -222.6699 |  | 0.98758 | -10.6074 | 61.7487 | -231.3212 |  | 1.0178 | -10.932 | 63.6382 | -238.3995 |  | 1.043 | -11.2025 | 65.2128 | -244.2981
| 7 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -53.3 | -4.2845 | -53.1275 |  | -1.9428 | 20.8675 | -3.1371 | 13.8887 |  | -1.9015 | 20.4231 | -3.0703 | 13.593 |  | -1.8567 | 19.9418 | -2.9979 | 13.2727 |  | -1.808 | 19.4188 | -2.9193 | 12.9246 |  | -1.7548 | 18.8483 | -2.8335 | 12.5449 |  | -1.6967 | 18.2237 | -2.7396 | 12.1291 |  | -1.6327 | 17.5367 | -2.6364 | 11.6719 |  | -1.5621 | 16.7776 | -2.5222 | 11.1667 |  | -1.4834 | 15.9324 | -2.3952 | 10.6041 |  | -0.86653 | 9.3072 | -1.3992 | 6.1946 |  | -0.47219 | 5.0717 | -0.76244 | 3.3755 |  | -0.19835 | 2.1305 | -0.32028 | 1.418 |  | 0.0028933 | -0.031076 | 0.1809 | -0.80091 |  | 0.15704 | -1.6867 | 9.8186 | -43.47 |  | 0.27888 | -2.9954 | 17.4369 | -77.1982 |  | 0.37761 | -4.0558 | 23.6102 | -104.5292 |  | 0.45924 | -4.9326 | 28.714 | -127.1255 |  | 0.63139 | -6.7816 | 39.4778 | -174.78 |  | 0.74616 | -8.0143 | 46.6537 | -206.5496 |  | 0.82814 | -8.8948 | 51.7793 | -229.2422 |  | 0.88962 | -9.5552 | 55.6235 | -246.2617 |  | 0.93744 | -10.0688 | 58.6135 | -259.499 |  | 0.9757 | -10.4797 | 61.0054 | -270.0889 |  | 1.007 | -10.8159 | 62.9625 | -278.7533 |  | 1.0331 | -11.096 | 64.5933 | -285.9737
| 8 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -61.5 | -4.9436 | -61.301 |  | -2.0099 | 21.588 | -3.2454 | 16.5788 |  | -1.9712 | 21.1724 | -3.1829 | 16.2596 |  | -1.9293 | 20.7222 | -3.1152 | 15.914 |  | -1.8838 | 20.233 | -3.0417 | 15.5383 |  | -1.8341 | 19.6995 | -2.9615 | 15.1285 |  | -1.7797 | 19.1153 | -2.8737 | 14.6799 |  | -1.7199 | 18.4728 | -2.7771 | 14.1864 |  | -1.6538 | 17.7628 | -2.6703 | 13.6412 |  | -1.5802 | 16.972 | -2.5515 | 13.0339 |  | -0.94202 | 10.118 | -1.5211 | 7.7703 |  | -0.53407 | 5.7363 | -0.86235 | 4.4053 |  | -0.25078 | 2.6935 | -0.40493 | 2.0685 |  | -0.042583 | 0.45737 | -0.068758 | 0.35124 |  | 0.11688 | -1.2554 | 7.308 | -37.3323 |  | 0.24293 | -2.6093 | 15.1893 | -77.5932 |  | 0.34507 | -3.7063 | 21.5757 | -110.2179 |  | 0.42952 | -4.6134 | 26.8558 | -137.1907 |  | 0.60762 | -6.5263 | 37.9913 | -194.0751 |  | 0.72635 | -7.8015 | 45.4149 | -231.9981 |  | 0.81116 | -8.7124 | 50.7175 | -259.0859 |  | 0.87476 | -9.3956 | 54.6944 | -279.4018 |  | 0.92423 | -9.9269 | 57.7876 | -295.203 |  | 0.96381 | -10.352 | 60.2621 | -307.844 |  | 0.99619 | -10.6998 | 62.2868 | -318.1866 |  | 1.0232 | -10.9896 | 63.9739 | -326.8055
| 9 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -69.7 | -5.6028 | -69.4744 |  | -2.077 | 22.3084 | -3.3537 | 19.4164 |  | -2.041 | 21.9216 | -3.2956 | 19.0797 |  | -2.002 | 21.5026 | -3.2326 | 18.715 |  | -1.9596 | 21.0473 | -3.1641 | 18.3187 |  | -1.9133 | 20.5507 | -3.0895 | 17.8865 |  | -1.8627 | 20.0069 | -3.0077 | 17.4132 |  | -1.807 | 19.4088 | -2.9178 | 16.8927 |  | -1.7455 | 18.748 | -2.8185 | 16.3175 |  | -1.6769 | 18.0117 | -2.7078 | 15.6766 |  | -1.0175 | 10.9289 | -1.643 | 9.5121 |  | -0.59595 | 6.4009 | -0.96227 | 5.5711 |  | -0.3032 | 3.2566 | -0.48958 | 2.8344 |  | -0.088059 | 0.94582 | -0.14219 | 0.8232 |  | 0.076727 | -0.82411 | 4.7974 | -27.7746 |  | 0.20698 | -2.2232 | 12.9417 | -74.9264 |  | 0.31254 | -3.3569 | 19.5413 | -113.1351 |  | 0.3998 | -4.2942 | 24.9976 | -144.7246 |  | 0.58384 | -6.2709 | 36.5047 | -211.3452 |  | 0.70653 | -7.5887 | 44.1761 | -255.759 |  | 0.79417 | -8.53 | 49.6556 | -287.4831 |  | 0.8599 | -9.236 | 53.7653 | -311.2762 |  | 0.91102 | -9.7851 | 56.9617 | -329.782 |  | 0.95192 | -10.2243 | 59.5188 | -344.5866 |  | 0.98538 | -10.5837 | 61.611 | -356.6994 |  | 1.0133 | -10.8832 | 63.3545 | -366.7934
wb | 10 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -77.9 | -6.2619 | -77.6479 | wb | -2.1441 | 23.0289 | -3.462 | 22.4015 | wb | -2.1107 | 22.6709 | -3.4082 | 22.0532 | wb | -2.0746 | 22.283 | -3.3499 | 21.676 | wb | -2.0354 | 21.8616 | -3.2865 | 21.266 | wb | -1.9926 | 21.4018 | -3.2174 | 20.8188 | wb | -1.9457 | 20.8985 | -3.1417 | 20.3291 | wb | -1.8942 | 20.3449 | -3.0585 | 19.7906 | wb | -1.8372 | 19.7332 | -2.9666 | 19.1956 | wb | -1.7737 | 19.0513 | -2.864 | 18.5323 | wb | -1.093 | 11.7398 | -1.7649 | 11.4199 | wb | -0.65783 | 7.0655 | -1.0622 | 6.873 | wb | -0.35563 | 3.8197 | -0.57423 | 3.7156 | wb | -0.13353 | 1.4343 | -0.21562 | 1.3952 | wb | 0.036573 | -0.39282 | 2.2867 | -14.7968 | wb | 0.17104 | -1.8371 | 10.6941 | -69.1979 | wb | 0.28 | -3.0074 | 17.5069 | -113.2809 | wb | 0.37008 | -3.975 | 23.1394 | -149.7271 | wb | 0.56007 | -6.0155 | 35.0181 | -226.5903 | wb | 0.68672 | -7.3759 | 42.9373 | -277.8324 | wb | 0.77719 | -8.3476 | 48.5938 | -314.4339 | wb | 0.84504 | -9.0764 | 52.8362 | -341.885 | wb | 0.89781 | -9.6432 | 56.1358 | -363.2359 | wb | 0.94003 | -10.0966 | 58.7756 | -380.3166 | wb | 0.97458 | -10.4677 | 60.9353 | -394.2917 | wb | 1.0034 | -10.7768 | 62.7351 | -405.9376
| 11 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -86.1 | -6.9211 | -85.8214 |  | -2.2112 | 23.7494 | -3.5703 | 25.5342 |  | -2.1805 | 23.4201 | -3.5208 | 25.1802 |  | -2.1473 | 23.0634 | -3.4672 | 24.7967 |  | -2.1112 | 22.6758 | -3.4089 | 24.3799 |  | -2.0718 | 22.253 | -3.3454 | 23.9254 |  | -2.0287 | 21.7901 | -3.2758 | 23.4276 |  | -1.9813 | 21.281 | -3.1992 | 22.8802 |  | -1.929 | 20.7184 | -3.1147 | 22.2754 |  | -1.8705 | 20.0909 | -3.0203 | 21.6008 |  | -1.1685 | 12.5507 | -1.8868 | 13.4938 |  | -0.71971 | 7.7302 | -1.1621 | 8.3111 |  | -0.40805 | 4.3828 | -0.65888 | 4.7121 |  | -0.17901 | 1.9227 | -0.28905 | 2.0672 |  | -0.0035806 | 0.038459 | -0.0057816 | 0.041349 |  | 0.13509 | -1.451 | 8.4465 | -60.4076 |  | 0.24746 | -2.6579 | 15.4724 | -110.6554 |  | 0.34036 | -3.6557 | 21.2812 | -152.1982 |  | 0.53629 | -5.7602 | 33.5315 | -239.8102 |  | 0.66691 | -7.1631 | 41.6984 | -298.2182 |  | 0.76021 | -8.1652 | 47.532 | -339.9381 |  | 0.83018 | -8.9168 | 51.9071 | -371.2281 |  | 0.88461 | -9.5013 | 55.31 | -395.5648 |  | 0.92815 | -9.969 | 58.0323 | -415.0341 |  | 0.96377 | -10.3516 | 60.2596 | -430.9635 |  | 0.99345 | -10.6704 | 62.1157 | -444.2381
| 12 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -94.3 | -7.5802 | -93.9948 |  | -2.2782 | 24.4699 | -3.6786 | 28.8145 |  | -2.2503 | 24.1694 | -3.6335 | 28.4606 |  | -2.2199 | 23.8438 | -3.5845 | 28.0772 |  | -2.187 | 23.4901 | -3.5313 | 27.6606 |  | -2.1511 | 23.1042 | -3.4733 | 27.2063 |  | -2.1117 | 22.6817 | -3.4098 | 26.7087 |  | -2.0685 | 22.217 | -3.34 | 26.1616 |  | -2.0207 | 21.7036 | -3.2628 | 25.557 |  | -1.9673 | 21.1305 | -3.1766 | 24.8822 |  | -1.244 | 13.3615 | -2.0087 | 15.7338 |  | -0.78158 | 8.3948 | -1.262 | 9.8853 |  | -0.46048 | 4.9458 | -0.74353 | 5.824 |  | -0.22449 | 2.4112 | -0.36248 | 2.8393 |  | -0.043735 | 0.46974 | -0.070618 | 0.55314 |  | 0.099143 | -1.0649 | 6.1989 | -48.5556 |  | 0.21492 | -2.3084 | 13.438 | -105.2584 |  | 0.31064 | -3.3365 | 19.4229 | -152.1381 |  | 0.51251 | -5.5048 | 32.045 | -251.005 |  | 0.6471 | -6.9503 | 40.4596 | -316.9164 |  | 0.74322 | -7.9828 | 46.4701 | -363.9959 |  | 0.81532 | -8.7572 | 50.978 | -399.3055 |  | 0.8714 | -9.3594 | 54.4841 | -426.7686 |  | 0.91626 | -9.8413 | 57.289 | -448.739 |  | 0.95296 | -10.2355 | 59.5839 | -466.7148 |  | 0.98355 | -10.564 | 61.4963 | -481.6947
| 13 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -102.5 | -8.2394 | -102.1683 |  | -2.3453 | 25.1904 | -3.787 | 32.2423 |  | -2.32 | 24.9186 | -3.7461 | 31.8944 |  | -2.2926 | 24.6242 | -3.7018 | 31.5176 |  | -2.2628 | 24.3043 | -3.6537 | 31.1081 |  | -2.2303 | 23.9554 | -3.6013 | 30.6615 |  | -2.1948 | 23.5733 | -3.5438 | 30.1724 |  | -2.1556 | 23.1531 | -3.4807 | 29.6346 |  | -2.1124 | 22.6888 | -3.4109 | 29.0403 |  | -2.0641 | 22.1702 | -3.3329 | 28.3765 |  | -1.3195 | 14.1724 | -2.1306 | 18.1398 |  | -0.84346 | 9.0594 | -1.3619 | 11.5955 |  | -0.5129 | 5.5089 | -0.82818 | 7.0511 |  | -0.26996 | 2.8996 | -0.43591 | 3.7113 |  | -0.083889 | 0.90103 | -0.13545 | 1.1533 |  | 0.063196 | -0.67877 | 3.9513 | -33.6418 |  | 0.18238 | -1.9589 | 11.4035 | -97.09 |  | 0.28092 | -3.0173 | 17.5647 | -149.5465 |  | 0.48874 | -5.2494 | 30.5584 | -260.1748 |  | 0.62728 | -6.7375 | 39.2208 | -333.927 |  | 0.72624 | -7.8004 | 45.4083 | -386.6072 |  | 0.80046 | -8.5976 | 50.0489 | -426.1173 |  | 0.85819 | -9.2176 | 53.6582 | -456.8474 |  | 0.90437 | -9.7136 | 56.5457 | -481.4314 |  | 0.94215 | -10.1194 | 58.9082 | -501.5457 |  | 0.97364 | -10.4576 | 60.8769 | -518.3075
| 14 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -110.7 | -8.8985 | -110.3418 |  | -2.4124 | 25.9109 | -3.8953 | 35.8176 |  | -2.3898 | 25.6679 | -3.8587 | 35.4817 |  | -2.3653 | 25.4046 | -3.8192 | 35.1178 |  | -2.3386 | 25.1186 | -3.7762 | 34.7223 |  | -2.3096 | 24.8065 | -3.7293 | 34.291 |  | -2.2778 | 24.4649 | -3.6779 | 33.8187 |  | -2.2428 | 24.0891 | -3.6214 | 33.2993 |  | -2.2041 | 23.674 | -3.559 | 32.7254 |  | -2.1609 | 23.2098 | -3.4892 | 32.0837 |  | -1.395 | 14.9833 | -2.2525 | 20.7119 |  | -0.90534 | 9.7241 | -1.4619 | 13.4419 |  | -0.56532 | 6.072 | -0.91282 | 8.3936 |  | -0.31544 | 3.3881 | -0.50934 | 4.6834 |  | -0.12404 | 1.3323 | -0.20029 | 1.8417 |  | 0.027249 | -0.29267 | 1.7037 | -15.6662 |  | 0.14985 | -1.6095 | 9.3691 | -86.1502 |  | 0.2512 | -2.6981 | 15.7065 | -144.4236 |  | 0.46496 | -4.994 | 29.0718 | -267.3195 |  | 0.60747 | -6.5247 | 37.982 | -349.2501 |  | 0.70926 | -7.618 | 44.3464 | -407.772 |  | 0.7856 | -8.4379 | 49.1198 | -451.6634 |  | 0.84498 | -9.0757 | 52.8323 | -485.8011 |  | 0.89248 | -9.5859 | 55.8024 | -513.1113 |  | 0.93135 | -10.0034 | 58.2325 | -535.456 |  | 0.96373 | -10.3512 | 60.2575 | -554.0766
| 15 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -118.9 | -9.5577 | -118.5152 |  | -2.4795 | 26.6314 | -4.0036 | 39.5405 |  | -2.4595 | 26.4171 | -3.9714 | 39.2224 |  | -2.4379 | 26.1851 | -3.9365 | 38.8778 |  | -2.4144 | 25.9328 | -3.8986 | 38.5033 |  | -2.3888 | 25.6577 | -3.8572 | 38.0948 |  | -2.3608 | 25.3565 | -3.8119 | 37.6476 |  | -2.3299 | 25.0252 | -3.7621 | 37.1557 |  | -2.2959 | 24.6591 | -3.7071 | 36.6122 |  | -2.2577 | 24.2494 | -3.6455 | 36.0039 |  | -1.4705 | 15.7941 | -2.3744 | 23.4501 |  | -0.96722 | 10.3887 | -1.5618 | 15.4244 |  | -0.61775 | 6.6351 | -0.99747 | 9.8513 |  | -0.36092 | 3.8765 | -0.58277 | 5.7556 |  | -0.1642 | 1.7636 | -0.26513 | 2.6185 |  | -0.008698 | 0.093423 | -0.014045 | 0.13871 |  | 0.11731 | -1.26 | 7.3346 | -72.439 |  | 0.22148 | -2.3789 | 13.8483 | -136.7694 |  | 0.44119 | -4.7387 | 27.5852 | -272.4391 |  | 0.58766 | -6.3119 | 36.7432 | -362.8856 |  | 0.69228 | -7.4356 | 43.2846 | -427.4903 |  | 0.77074 | -8.2783 | 48.1906 | -475.9438 |  | 0.83177 | -8.9338 | 52.0065 | -513.6298 |  | 0.88059 | -9.4582 | 55.0591 | -543.7786 |  | 0.92054 | -9.8873 | 57.5567 | -568.4459 |  | 0.95383 | -10.2448 | 59.6381 | -589.0019
| 16 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -127.1 | -10.2168 | -126.6887 |  | -2.5466 | 27.3519 | -4.1119 | 43.411 |  | -2.5293 | 27.1664 | -4.084 | 43.1166 |  | -2.5106 | 26.9655 | -4.0538 | 42.7976 |  | -2.4902 | 26.7471 | -4.021 | 42.451 |  | -2.4681 | 26.5089 | -3.9852 | 42.073 |  | -2.4438 | 26.2481 | -3.946 | 41.6591 |  | -2.4171 | 25.9613 | -3.9028 | 41.2038 |  | -2.3876 | 25.6443 | -3.8552 | 40.7008 |  | -2.3545 | 25.289 | -3.8018 | 40.1369 |  | -1.546 | 16.605 | -2.4963 | 26.3543 |  | -1.0291 | 11.0533 | -1.6617 | 17.543 |  | -0.67017 | 7.1982 | -1.0821 | 11.4244 |  | -0.40639 | 4.3649 | -0.6562 | 6.9277 |  | -0.20435 | 2.1949 | -0.32996 | 3.4835 |  | -0.044645 | 0.47952 | -0.072088 | 0.76106 |  | 0.084769 | -0.91049 | 5.3002 | -55.9564 |  | 0.19176 | -2.0597 | 11.9901 | -126.5838 |  | 0.41741 | -4.4833 | 26.0987 | -275.5337 |  | 0.56784 | -6.0991 | 35.5044 | -374.8336 |  | 0.67529 | -7.2532 | 42.2228 | -445.7621 |  | 0.75588 | -8.1187 | 47.2615 | -498.9585 |  | 0.81856 | -8.792 | 51.1806 | -540.3335 |  | 0.86871 | -9.3305 | 54.3158 | -573.4334 |  | 0.90973 | -9.7712 | 56.881 | -600.5152 |  | 0.94392 | -10.1384 | 59.0187 | -623.0834
| 17 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -135.3 | -10.876 | -134.8622 |  | -2.6136 | 28.0724 | -4.2202 | 47.429 |  | -2.599 | 27.9157 | -4.1967 | 47.1641 |  | -2.5832 | 27.7459 | -4.1711 | 46.8773 |  | -2.5661 | 27.5613 | -4.1434 | 46.5655 |  | -2.5473 | 27.3601 | -4.1131 | 46.2255 |  | -2.5268 | 27.1397 | -4.08 | 45.8531 |  | -2.5042 | 26.8973 | -4.0436 | 45.4436 |  | -2.4793 | 26.6295 | -4.0033 | 44.9912 |  | -2.4513 | 26.3286 | -3.9581 | 44.4829 |  | -1.6215 | 17.4159 | -2.6182 | 29.4245 |  | -1.091 | 11.7179 | -1.7616 | 19.7977 |  | -0.7226 | 7.7612 | -1.1668 | 13.1128 |  | -0.45187 | 4.8534 | -0.72963 | 8.1999 |  | -0.2445 | 2.6262 | -0.3948 | 4.437 |  | -0.080592 | 0.86562 | -0.13013 | 1.4625 |  | 0.052231 | -0.561 | 3.2658 | -36.7023 |  | 0.16204 | -1.7405 | 10.1318 | -113.8668 |  | 0.39364 | -4.2279 | 24.6121 | -276.6031 |  | 0.54803 | -5.8862 | 34.2656 | -385.094 |  | 0.65831 | -7.0708 | 41.1609 | -462.5874 |  | 0.74102 | -7.9591 | 46.3324 | -520.7075 |  | 0.80535 | -8.6501 | 50.3547 | -565.9121 |  | 0.85682 | -9.2029 | 53.5725 | -602.0757 |  | 0.89893 | -9.6551 | 56.2053 | -631.6641 |  | 0.93401 | -10.032 | 58.3993 | -656.3211
| 18 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -143.5 | -11.5351 | -143.0356 |  | -2.6807 | 28.7929 | -4.3285 | 51.5946 |  | -2.6688 | 28.6649 | -4.3093 | 51.3652 |  | -2.6559 | 28.5263 | -4.2884 | 51.1167 |  | -2.6419 | 28.3756 | -4.2658 | 50.8467 |  | -2.6266 | 28.2112 | -4.2411 | 50.5522 |  | -2.6098 | 28.0313 | -4.214 | 50.2298 |  | -2.5914 | 27.8334 | -4.1843 | 49.8752 |  | -2.571 | 27.6147 | -4.1514 | 49.4833 |  | -2.5481 | 27.3683 | -4.1144 | 49.0417 |  | -1.697 | 18.2267 | -2.7401 | 32.6608 |  | -1.1529 | 12.3826 | -1.8615 | 22.1886 |  | -0.77502 | 8.3243 | -1.2514 | 14.9165 |  | -0.49734 | 5.3418 | -0.80306 | 9.5721 |  | -0.28466 | 3.0574 | -0.45964 | 5.4787 |  | -0.11654 | 1.2517 | -0.18817 | 2.243 |  | 0.019693 | -0.21152 | 1.2313 | -14.6769 |  | 0.13233 | -1.4213 | 8.2736 | -98.6186 |  | 0.36986 | -3.9726 | 23.1255 | -275.6475 |  | 0.52822 | -5.6734 | 33.0267 | -393.6668 |  | 0.64133 | -6.8883 | 40.0991 | -477.9663 |  | 0.72616 | -7.7995 | 45.4033 | -541.1909 |  | 0.79214 | -8.5082 | 49.5288 | -590.3656 |  | 0.84493 | -9.0752 | 52.8292 | -629.7054 |  | 0.88812 | -9.539 | 55.5296 | -661.8925 |  | 0.92411 | -9.9256 | 57.7799 | -688.715
| 19 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -151.7 | -12.1943 | -151.2091 |  | -2.7478 | 29.5134 | -4.4368 | 55.9077 |  | -2.7386 | 29.4142 | -4.4219 | 55.7197 |  | -2.7286 | 29.3067 | -4.4058 | 55.516 |  | -2.7177 | 29.1898 | -4.3882 | 55.2947 |  | -2.7058 | 29.0624 | -4.369 | 55.0533 |  | -2.6928 | 28.9229 | -4.3481 | 54.789 |  | -2.6785 | 28.7694 | -4.325 | 54.4984 |  | -2.6627 | 28.5999 | -4.2995 | 54.1772 |  | -2.6449 | 28.4079 | -4.2707 | 53.8135 |  | -1.7725 | 19.0376 | -2.862 | 36.0632 |  | -1.2147 | 13.0472 | -1.9614 | 24.7155 |  | -0.82745 | 8.8874 | -1.3361 | 16.8355 |  | -0.54282 | 5.8303 | -0.87649 | 11.0444 |  | -0.32481 | 3.4887 | -0.52447 | 6.6087 |  | -0.15249 | 1.6378 | -0.24622 | 3.1025 |  | -0.012845 | 0.13796 | -0.02074 | 0.26134 |  | 0.10261 | -1.1021 | 6.4154 | -80.8389 |  | 0.34608 | -3.7172 | 21.6389 | -272.6668 |  | 0.5084 | -5.4606 | 31.7879 | -400.5521 |  | 0.62435 | -6.7059 | 39.0372 | -491.8987 |  | 0.7113 | -7.6399 | 44.4742 | -560.4086 |  | 0.77894 | -8.3663 | 48.703 | -613.6941 |  | 0.83304 | -8.9475 | 52.086 | -656.3226 |  | 0.87731 | -9.423 | 54.8539 | -691.2004 |  | 0.9142 | -9.8192 | 57.1605 | -720.2652
| 20 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -159.9 | -12.8534 | -159.3826 |  | -2.8149 | 30.2339 | -4.5452 | 60.3683 |  | -2.8083 | 30.1634 | -4.5346 | 60.2276 |  | -2.8012 | 30.0871 | -4.5231 | 60.0751 |  | -2.7935 | 30.0041 | -4.5106 | 59.9094 |  | -2.7851 | 29.9136 | -4.497 | 59.7287 |  | -2.7758 | 29.8145 | -4.4821 | 59.5309 |  | -2.7657 | 29.7055 | -4.4657 | 59.3133 |  | -2.7545 | 29.5851 | -4.4476 | 59.0728 |  | -2.7417 | 29.4475 | -4.4269 | 58.7981 |  | -1.848 | 19.8485 | -2.9839 | 39.6317 |  | -1.2766 | 13.7118 | -2.0613 | 27.3786 |  | -0.87987 | 9.4505 | -1.4207 | 18.8698 |  | -0.5883 | 6.3187 | -0.94992 | 12.6167 |  | -0.36497 | 3.92 | -0.58931 | 7.8271 |  | -0.18843 | 2.0239 | -0.30426 | 4.0412 |  | -0.045383 | 0.48745 | -0.073279 | 0.97329 |  | 0.072886 | -0.78285 | 4.5572 | -60.5279 |  | 0.32231 | -3.4618 | 20.1523 | -267.661 |  | 0.48859 | -5.2478 | 30.5491 | -405.7497 |  | 0.60736 | -6.5235 | 37.9754 | -504.3845 |  | 0.69644 | -7.4803 | 43.5451 | -578.3606 |  | 0.76573 | -8.2245 | 47.8771 | -635.8976 |  | 0.82115 | -8.8198 | 51.3427 | -681.9272 |  | 0.8665 | -9.3069 | 54.1782 | -719.5878 |  | 0.9043 | -9.7128 | 56.5411 | -750.9716
| 1 | 8 | 4 | 32 | 0.22 | 0 | -166 | -13.3438 | -165.4628 |  | -2.8648 | 30.7699 | -6.7694 | 93.34 |  | -2.8602 | 30.7208 | -6.7586 | 93.191 |  | -2.8553 | 30.6676 | -6.7469 | 93.0297 |  | -2.8499 | 30.6098 | -6.7342 | 92.8544 |  | -2.844 | 30.5468 | -6.7203 | 92.6632 |  | -2.8376 | 30.4778 | -6.7051 | 92.4538 |  | -2.8305 | 30.4018 | -6.6884 | 92.2235 |  | -2.8227 | 30.318 | -6.67 | 91.9691 |  | -2.8137 | 30.2209 | -6.6486 | 91.6746 |  | -1.9041 | 20.4517 | -4.4994 | 62.0399 |  | -1.3227 | 14.2063 | -3.1254 | 43.0945 |  | -0.91887 | 9.8693 | -2.1713 | 29.9385 |  | -0.62213 | 6.6821 | -1.4701 | 20.27 |  | -0.39484 | 4.2408 | -0.93299 | 12.8645 |  | -0.21517 | 2.3111 | -0.50845 | 7.0108 |  | -0.069588 | 0.74743 | -0.16443 | 2.2673 |  | 0.050777 | -0.54538 | 1.6249 | -22.4046 |  | 0.30462 | -3.2719 | 9.7479 | -134.4095 |  | 0.47385 | -5.0895 | 15.1632 | -209.0795 |  | 0.59473 | -6.3878 | 19.0314 | -262.4151 |  | 0.68539 | -7.3616 | 21.9324 | -302.4169 |  | 0.7559 | -8.1189 | 24.1888 | -333.5293 |  | 0.81231 | -8.7248 | 25.9939 | -358.4193 |  | 0.85846 | -9.2205 | 27.4709 | -378.7839 |  | 0.89693 | -9.6336 | 28.7016 | -395.7543
| 2 | 8 | 4 | 32 | 0.22 | 0 | -170 | -13.6653 | -169.4499 |  | -2.8975 | 31.1213 | -6.8467 | 96.681 |  | -2.8942 | 31.0863 | -6.839 | 96.572 |  | -2.8907 | 31.0483 | -6.8306 | 96.454 |  | -2.8869 | 31.007 | -6.8215 | 96.3258 |  | -2.8827 | 30.962 | -6.8116 | 96.1859 |  | -2.8781 | 30.9127 | -6.8008 | 96.0327 |  | -2.873 | 30.8585 | -6.7889 | 95.8643 |  | -2.8675 | 30.7986 | -6.7757 | 95.6782 |  | -2.8609 | 30.728 | -6.7602 | 95.4591 |  | -1.941 | 20.8472 | -4.5864 | 64.7637 |  | -1.3528 | 14.5305 | -3.1967 | 45.1401 |  | -0.94444 | 10.144 | -2.2317 | 31.5132 |  | -0.64431 | 6.9204 | -1.5225 | 21.4986 |  | -0.41442 | 4.4512 | -0.97927 | 13.8281 |  | -0.23271 | 2.4995 | -0.54988 | 7.7648 |  | -0.08546 | 0.91791 | -0.20194 | 2.8516 |  | 0.03628 | -0.38967 | 1.161 | -16.3936 |  | 0.29302 | -3.1473 | 9.3768 | -132.4076 |  | 0.46419 | -4.9857 | 14.854 | -209.7503 |  | 0.58645 | -6.2989 | 18.7663 | -264.995 |  | 0.67814 | -7.2837 | 21.7005 | -306.4286 |  | 0.74946 | -8.0497 | 23.9826 | -338.6547 |  | 0.80651 | -8.6625 | 25.8084 | -364.4356 |  | 0.85319 | -9.1639 | 27.3022 | -385.529 |  | 0.89209 | -9.5817 | 28.547 | -403.1069
ab | 3 | 8 | 4 | 32 | 0.22 | 0 | -174 | -13.9868 | -173.4369 | ab | -2.9302 | 31.4728 | -6.924 | 100.0734 | ab | -2.9283 | 31.4518 | -6.9194 | 100.0065 | ab | -2.9261 | 31.429 | -6.9144 | 99.934 | ab | -2.9238 | 31.4042 | -6.9089 | 99.8552 | ab | -2.9213 | 31.3772 | -6.903 | 99.7693 | ab | -2.9186 | 31.3476 | -6.8965 | 99.6753 | ab | -2.9155 | 31.3151 | -6.8893 | 99.5718 | ab | -2.9122 | 31.2791 | -6.8814 | 99.4575 | ab | -2.9081 | 31.2352 | -6.8717 | 99.3177 | ab | -1.9778 | 21.2428 | -4.6734 | 67.5452 | ab | -1.383 | 14.8547 | -3.268 | 47.2331 | ab | -0.97002 | 10.4187 | -2.2921 | 33.1281 | ab | -0.66649 | 7.1586 | -1.5749 | 22.7621 | ab | -0.43401 | 4.6616 | -1.0256 | 14.8224 | ab | -0.25024 | 2.6878 | -0.59132 | 8.5464 | ab | -0.10133 | 1.0884 | -0.23944 | 3.4607 | ab | 0.021782 | -0.23396 | 0.69704 | -10.0743 | ab | 0.28143 | -3.0227 | 9.0056 | -130.1591 | ab | 0.45452 | -4.8819 | 14.5447 | -210.2156 | ab | 0.57816 | -6.2099 | 18.5012 | -267.3988 | ab | 0.67089 | -7.2059 | 21.4685 | -310.2862 | ab | 0.74301 | -7.9805 | 23.7765 | -343.643 | ab | 0.80071 | -8.6003 | 25.6228 | -370.3285 | ab | 0.84792 | -9.1073 | 27.1335 | -392.1621 | ab | 0.88726 | -9.5298 | 28.3923 | -410.3568
| 4 | 8 | 4 | 32 | 0.22 | 0 | -178 | -14.3084 | -177.424 |  | -2.9629 | 31.8243 | -7.0013 | 103.5171 |  | -2.9623 | 31.8173 | -6.9998 | 103.4943 |  | -2.9616 | 31.8097 | -6.9981 | 103.4696 |  | -2.9608 | 31.8014 | -6.9963 | 103.4427 |  | -2.96 | 31.7924 | -6.9943 | 103.4135 |  | -2.9591 | 31.7825 | -6.9922 | 103.3814 |  | -2.9581 | 31.7717 | -6.9898 | 103.3461 |  | -2.9569 | 31.7597 | -6.9871 | 103.3071 |  | -2.9553 | 31.7423 | -6.9833 | 103.2505 |  | -2.0146 | 21.6383 | -4.7604 | 70.3846 |  | -1.4132 | 15.1789 | -3.3394 | 49.3735 |  | -0.99559 | 10.6934 | -2.3525 | 34.7831 |  | -0.68868 | 7.3969 | -1.6273 | 24.0604 |  | -0.4536 | 4.872 | -1.0718 | 15.8475 |  | -0.26778 | 2.8762 | -0.63275 | 9.3555 |  | -0.1172 | 1.2589 | -0.27695 | 4.0948 |  | 0.0072851 | -0.078247 | 0.23312 | -3.4468 |  | 0.26983 | -2.8982 | 8.6345 | -127.6639 |  | 0.44486 | -4.7781 | 14.2354 | -210.4753 |  | 0.56988 | -6.1209 | 18.2361 | -269.6263 |  | 0.66364 | -7.128 | 21.2366 | -313.9896 |  | 0.73657 | -7.9113 | 23.5703 | -348.4944 |  | 0.79491 | -8.538 | 25.4372 | -376.0982 |  | 0.84265 | -9.0507 | 26.9648 | -398.6831 |  | 0.88243 | -9.4779 | 28.2377 | -417.5039
| 1 | 3.6 | 7.625 | 27.45 | 0.0465 | -38.2 | -176 | -52.224 | -172.3598 |  | -2.9214 | 31.3779 | -1.4591 | 20.9571 |  | -2.9191 | 31.353 | -1.4579 | 20.9405 |  | -2.9166 | 31.3261 | -1.4567 | 20.9225 |  | -2.9138 | 31.2969 | -1.4553 | 20.903 |  | -2.9109 | 31.265 | -1.4538 | 20.8817 |  | -2.9076 | 31.2301 | -1.4522 | 20.8584 |  | -2.9041 | 31.1917 | -1.4504 | 20.8328 |  | -2.9001 | 31.1493 | -1.4484 | 20.8044 |  | -2.8953 | 31.0982 | -1.4461 | 20.7703 |  | -1.9678 | 21.1359 | -0.98282 | 14.1166 |  | -1.3749 | 14.7671 | -0.68667 | 9.8629 |  | -0.96311 | 10.3445 | -0.48102 | 6.909 |  | -0.6605 | 7.0943 | -0.32988 | 4.7382 |  | -0.42872 | 4.6048 | -0.21412 | 3.0755 |  | -0.24551 | 2.6369 | -0.12262 | 1.7612 |  | -0.097044 | 1.0423 | -0.048468 | 0.69617 |  | 0.025699 | -0.27603 | 0.70544 | -10.1325 |  | 0.28456 | -3.0564 | 7.8112 | -112.194 |  | 0.45713 | -4.9099 | 12.5483 | -180.2351 |  | 0.5804 | -6.2339 | 15.932 | -228.8358 |  | 0.67285 | -7.2269 | 18.4697 | -265.2864 |  | 0.74476 | -7.9992 | 20.4435 | -293.6368 |  | 0.80228 | -8.6171 | 22.0226 | -316.3172 |  | 0.84935 | -9.1226 | 23.3145 | -334.8738 |  | 0.88857 | -9.5439 | 24.3911 | -350.3377
| 2 | 3.6 | 7.625 | 27.45 | 0.0465 | -34.6 | -176 | -48.6357 | -172.6492 |  | -2.9238 | 31.4034 | -1.4603 | 21.0093 |  | -2.9215 | 31.3796 | -1.4591 | 20.9934 |  | -2.9191 | 31.3538 | -1.4579 | 20.9762 |  | -2.9165 | 31.3257 | -1.4566 | 20.9574 |  | -2.9137 | 31.2952 | -1.4552 | 20.9369 |  | -2.9106 | 31.2617 | -1.4537 | 20.9145 |  | -2.9071 | 31.2249 | -1.452 | 20.8899 |  | -2.9034 | 31.1842 | -1.4501 | 20.8627 |  | -2.8988 | 31.135 | -1.4478 | 20.8298 |  | -1.9705 | 21.1646 | -0.98416 | 14.1595 |  | -1.3771 | 14.7906 | -0.68776 | 9.8952 |  | -0.96496 | 10.3644 | -0.48195 | 6.934 |  | -0.66211 | 7.1115 | -0.33069 | 4.7577 |  | -0.43014 | 4.62 | -0.21483 | 3.0909 |  | -0.24678 | 2.6506 | -0.12325 | 1.7733 |  | -0.098196 | 1.0547 | -0.049044 | 0.70561 |  | 0.024647 | -0.26473 | 0.67656 | -9.7339 |  | 0.28372 | -3.0473 | 7.788 | -112.0499 |  | 0.45643 | -4.9024 | 12.529 | -180.2606 |  | 0.5798 | -6.2275 | 15.9155 | -228.9826 |  | 0.67232 | -7.2213 | 18.4553 | -265.524 |  | 0.74429 | -7.9942 | 20.4307 | -293.9451 |  | 0.80186 | -8.6126 | 22.011 | -316.682 |  | 0.84896 | -9.1185 | 23.304 | -335.285 |  | 0.88822 | -9.5401 | 24.3815 | -350.7874
| 3 | 3.6 | 7.625 | 27.45 | 0.0465 | -31 | -176 | -45.0473 | -172.9385 |  | -2.9261 | 31.4289 | -1.4614 | 21.0616 |  | -2.924 | 31.4061 | -1.4604 | 21.0464 |  | -2.9217 | 31.3814 | -1.4592 | 21.0298 |  | -2.9192 | 31.3546 | -1.458 | 21.0118 |  | -2.9165 | 31.3253 | -1.4566 | 20.9922 |  | -2.9135 | 31.2932 | -1.4551 | 20.9708 |  | -2.9102 | 31.258 | -1.4535 | 20.9471 |  | -2.9066 | 31.2191 | -1.4517 | 20.921 |  | -2.9022 | 31.1718 | -1.4495 | 20.8893 |  | -1.9732 | 21.1933 | -0.98549 | 14.2024 |  | -1.3792 | 14.8142 | -0.68886 | 9.9275 |  | -0.96682 | 10.3844 | -0.48287 | 6.9589 |  | -0.66372 | 7.1288 | -0.33149 | 4.7773 |  | -0.43156 | 4.6353 | -0.21554 | 3.1063 |  | -0.24805 | 2.6643 | -0.12389 | 1.7854 |  | -0.099348 | 1.0671 | -0.049619 | 0.71509 |  | 0.023595 | -0.25342 | 0.64767 | -9.334 |  | 0.28288 | -3.0383 | 7.7649 | -111.9048 |  | 0.45573 | -4.8949 | 12.5098 | -180.2853 |  | 0.5792 | -6.221 | 15.899 | -229.1285 |  | 0.6718 | -7.2156 | 18.4408 | -265.7609 |  | 0.74382 | -7.9892 | 20.4179 | -294.2528 |  | 0.80144 | -8.608 | 21.9995 | -317.0463 |  | 0.84858 | -9.1144 | 23.2935 | -335.6956 |  | 0.88786 | -9.5363 | 24.3719 | -351.2366
| 4 | 3.6 | 7.625 | 27.45 | 0.0465 | -27.4 | -176 | -41.4589 | -173.2279 |  | -2.9285 | 31.4544 | -1.4626 | 21.114 |  | -2.9265 | 31.4326 | -1.4616 | 21.0994 |  | -2.9243 | 31.409 | -1.4605 | 21.0836 |  | -2.9219 | 31.3834 | -1.4593 | 21.0664 |  | -2.9193 | 31.3554 | -1.458 | 21.0476 |  | -2.9164 | 31.3248 | -1.4566 | 21.027 |  | -2.9133 | 31.2911 | -1.455 | 21.0044 |  | -2.9098 | 31.2539 | -1.4533 | 20.9795 |  | -2.9056 | 31.2086 | -1.4512 | 20.949 |  | -1.9758 | 21.2221 | -0.98683 | 14.2455 |  | -1.3814 | 14.8377 | -0.68995 | 9.9599 |  | -0.96868 | 10.4043 | -0.4838 | 6.984 |  | -0.66533 | 7.1461 | -0.3323 | 4.7969 |  | -0.43298 | 4.6506 | -0.21625 | 3.1217 |  | -0.24933 | 2.6779 | -0.12452 | 1.7976 |  | -0.1005 | 1.0794 | -0.050194 | 0.72459 |  | 0.022542 | -0.24212 | 0.61879 | -8.9326 |  | 0.28203 | -3.0293 | 7.7418 | -111.7584 |  | 0.45503 | -4.8873 | 12.4905 | -180.309 |  | 0.5786 | -6.2145 | 15.8825 | -229.2737 |  | 0.67127 | -7.2099 | 18.4264 | -265.9972 |  | 0.74335 | -7.9842 | 20.405 | -294.5599 |  | 0.80102 | -8.6035 | 21.9879 | -317.4101 |  | 0.8482 | -9.1103 | 23.283 | -336.1057 |  | 0.88751 | -9.5326 | 24.3623 | -351.6854
b21 | 5 | 3.6 | 7.625 | 27.45 | 0.0465 | -23.8 | -176 | -37.8706 | -173.5173 | b21 | -2.9309 | 31.4799 | -1.4638 | 21.1664 | b21 | -2.929 | 31.4591 | -1.4628 | 21.1525 | b21 | -2.9269 | 31.4366 | -1.4618 | 21.1374 | b21 | -2.9246 | 31.4122 | -1.4607 | 21.1209 | b21 | -2.9221 | 31.3856 | -1.4594 | 21.103 | b21 | -2.9194 | 31.3564 | -1.4581 | 21.0834 | b21 | -2.9164 | 31.3243 | -1.4566 | 21.0618 | b21 | -2.9131 | 31.2888 | -1.4549 | 21.038 | b21 | -2.9091 | 31.2454 | -1.4529 | 21.0088 | b21 | -1.9785 | 21.2508 | -0.98816 | 14.2886 | b21 | -1.3836 | 14.8612 | -0.69105 | 9.9924 | b21 | -0.97053 | 10.4242 | -0.48473 | 7.009 | b21 | -0.66694 | 7.1634 | -0.3331 | 4.8165 | b21 | -0.43441 | 4.6658 | -0.21696 | 3.1372 | b21 | -0.2506 | 2.6916 | -0.12516 | 1.8098 | b21 | -0.10165 | 1.0918 | -0.05077 | 0.73412 | b21 | 0.02149 | -0.23082 | 0.5899 | -8.5299 | b21 | 0.28119 | -3.0202 | 7.7187 | -111.611 | b21 | 0.45433 | -4.8798 | 12.4713 | -180.3318 | b21 | 0.57799 | -6.2081 | 15.8659 | -229.418 | b21 | 0.67075 | -7.2043 | 18.412 | -266.2327 | b21 | 0.74288 | -7.9791 | 20.3922 | -294.8664 | b21 | 0.8006 | -8.599 | 21.9764 | -317.7733 | b21 | 0.84781 | -9.1062 | 23.2725 | -336.5153 | b21 | 0.88716 | -9.5288 | 24.3526 | -352.1336
| 6 | 3.6 | 7.625 | 27.45 | 0.0465 | -20.2 | -176 | -34.2822 | -173.8067 |  | -2.9333 | 31.5054 | -1.465 | 21.2189 |  | -2.9314 | 31.4857 | -1.4641 | 21.2056 |  | -2.9294 | 31.4643 | -1.4631 | 21.1912 |  | -2.9273 | 31.441 | -1.462 | 21.1756 |  | -2.9249 | 31.4157 | -1.4608 | 21.1585 |  | -2.9223 | 31.3879 | -1.4595 | 21.1398 |  | -2.9195 | 31.3574 | -1.4581 | 21.1193 |  | -2.9163 | 31.3237 | -1.4566 | 21.0965 |  | -2.9125 | 31.2822 | -1.4546 | 21.0686 |  | -1.9812 | 21.2795 | -0.9895 | 14.3317 |  | -1.3858 | 14.8847 | -0.69214 | 10.0249 |  | -0.97239 | 10.4442 | -0.48565 | 7.0342 |  | -0.66855 | 7.1807 | -0.3339 | 4.8362 |  | -0.43583 | 4.6811 | -0.21767 | 3.1527 |  | -0.25187 | 2.7053 | -0.1258 | 1.822 |  | -0.1028 | 1.1042 | -0.051345 | 0.74368 |  | 0.020438 | -0.21952 | 0.56102 | -8.1258 |  | 0.28035 | -3.0112 | 7.6956 | -111.4625 |  | 0.45363 | -4.8723 | 12.452 | -180.3536 |  | 0.57739 | -6.2016 | 15.8494 | -229.5616 |  | 0.67022 | -7.1986 | 18.3975 | -266.4675 |  | 0.74242 | -7.9741 | 20.3793 | -295.1722 |  | 0.80018 | -8.5945 | 21.9648 | -318.1359 |  | 0.84743 | -9.102 | 23.262 | -336.9244 |  | 0.88681 | -9.525 | 24.343 | -352.5815
| 7 | 3.6 | 7.625 | 27.45 | 0.0465 | -16.6 | -176 | -30.6939 | -174.0961 |  | -2.9356 | 31.5309 | -1.4662 | 21.2715 |  | -2.9339 | 31.5122 | -1.4653 | 21.2588 |  | -2.932 | 31.4919 | -1.4644 | 21.2451 |  | -2.93 | 31.4699 | -1.4633 | 21.2303 |  | -2.9277 | 31.4458 | -1.4622 | 21.2141 |  | -2.9253 | 31.4195 | -1.461 | 21.1963 |  | -2.9226 | 31.3906 | -1.4597 | 21.1768 |  | -2.9196 | 31.3586 | -1.4582 | 21.1552 |  | -2.9159 | 31.319 | -1.4563 | 21.1285 |  | -1.9839 | 21.3082 | -0.99083 | 14.375 |  | -1.388 | 14.9083 | -0.69323 | 10.0575 |  | -0.97424 | 10.4641 | -0.48658 | 7.0593 |  | -0.67016 | 7.198 | -0.33471 | 4.8559 |  | -0.43725 | 4.6964 | -0.21838 | 3.1683 |  | -0.25314 | 2.719 | -0.12643 | 1.8343 |  | -0.10396 | 1.1166 | -0.051921 | 0.75326 |  | 0.019386 | -0.20822 | 0.53214 | -7.7203 |  | 0.27951 | -3.0021 | 7.6725 | -111.3128 |  | 0.45292 | -4.8647 | 12.4328 | -180.3745 |  | 0.57679 | -6.1952 | 15.8329 | -229.7043 |  | 0.66969 | -7.193 | 18.3831 | -266.7017 |  | 0.74195 | -7.9691 | 20.3665 | -295.4774 |  | 0.79975 | -8.59 | 21.9533 | -318.498 |  | 0.84705 | -9.0979 | 23.2515 | -337.333 |  | 0.88646 | -9.5213 | 24.3334 | -353.0288
| 8 | 3.6 | 7.625 | 27.45 | 0.0465 | -13 | -176 | -27.1055 | -174.3855 |  | -2.938 | 31.5564 | -1.4674 | 21.3241 |  | -2.9364 | 31.5387 | -1.4666 | 21.3121 |  | -2.9346 | 31.5195 | -1.4657 | 21.2991 |  | -2.9326 | 31.4987 | -1.4647 | 21.285 |  | -2.9305 | 31.476 | -1.4636 | 21.2697 |  | -2.9282 | 31.4511 | -1.4625 | 21.2529 |  | -2.9257 | 31.4237 | -1.4612 | 21.2344 |  | -2.9228 | 31.3935 | -1.4598 | 21.2139 |  | -2.9193 | 31.3558 | -1.458 | 21.1885 |  | -1.9865 | 21.3369 | -0.99217 | 14.4183 |  | -1.3902 | 14.9318 | -0.69433 | 10.0901 |  | -0.9761 | 10.484 | -0.48751 | 7.0845 |  | -0.67177 | 7.2153 | -0.33551 | 4.8757 |  | -0.43867 | 4.7117 | -0.21909 | 3.1839 |  | -0.25442 | 2.7326 | -0.12707 | 1.8466 |  | -0.10511 | 1.1289 | -0.052496 | 0.76288 |  | 0.018333 | -0.19692 | 0.50325 | -7.3133 |  | 0.27867 | -2.9931 | 7.6494 | -111.1621 |  | 0.45222 | -4.8572 | 12.4135 | -180.3945 |  | 0.57619 | -6.1887 | 15.8164 | -229.8463 |  | 0.66917 | -7.1873 | 18.3686 | -266.9351 |  | 0.74148 | -7.9641 | 20.3537 | -295.782 |  | 0.79933 | -8.5854 | 21.9417 | -318.8595 |  | 0.84667 | -9.0938 | 23.241 | -337.7411 |  | 0.88611 | -9.5175 | 24.3238 | -353.4757
| 9 | 3.6 | 7.625 | 27.45 | 0.0465 | -9.4 | -176 | -23.5172 | -174.6748 |  | -2.9404 | 31.5819 | -1.4686 | 21.3767 |  | -2.9388 | 31.5652 | -1.4678 | 21.3654 |  | -2.9372 | 31.5472 | -1.4669 | 21.3532 |  | -2.9353 | 31.5275 | -1.466 | 21.3399 |  | -2.9333 | 31.5061 | -1.465 | 21.3254 |  | -2.9311 | 31.4826 | -1.4639 | 21.3095 |  | -2.9287 | 31.4568 | -1.4627 | 21.292 |  | -2.9261 | 31.4283 | -1.4614 | 21.2727 |  | -2.9228 | 31.3926 | -1.4598 | 21.2486 |  | -1.9892 | 21.3656 | -0.9935 | 14.4616 |  | -1.3924 | 14.9553 | -0.69542 | 10.1227 |  | -0.97796 | 10.504 | -0.48843 | 7.1098 |  | -0.67338 | 7.2326 | -0.33632 | 4.8955 |  | -0.44009 | 4.7269 | -0.2198 | 3.1995 |  | -0.25569 | 2.7463 | -0.1277 | 1.8589 |  | -0.10626 | 1.1413 | -0.053071 | 0.77252 |  | 0.017281 | -0.18561 | 0.47437 | -6.905 |  | 0.27782 | -2.984 | 7.6263 | -111.0102 |  | 0.45152 | -4.8497 | 12.3942 | -180.4136 |  | 0.57559 | -6.1823 | 15.7999 | -229.9875 |  | 0.66864 | -7.1817 | 18.3542 | -267.1679 |  | 0.74101 | -7.959 | 20.3408 | -296.086 |  | 0.79891 | -8.5809 | 21.9301 | -319.2204 |  | 0.84628 | -9.0897 | 23.2305 | -338.1486 |  | 0.88576 | -9.5137 | 24.3141 | -353.9221
| 10 | 3.6 | 7.625 | 27.45 | 0.0465 | -5.8 | -176 | -19.9288 | -174.9642 |  | -2.9428 | 31.6074 | -1.4697 | 21.4294 |  | -2.9413 | 31.5918 | -1.469 | 21.4188 |  | -2.9397 | 31.5748 | -1.4682 | 21.4073 |  | -2.938 | 31.5564 | -1.4674 | 21.3948 |  | -2.9361 | 31.5362 | -1.4664 | 21.3811 |  | -2.9341 | 31.5142 | -1.4654 | 21.3662 |  | -2.9318 | 31.49 | -1.4643 | 21.3498 |  | -2.9293 | 31.4632 | -1.463 | 21.3316 |  | -2.9262 | 31.4294 | -1.4615 | 21.3087 |  | -1.9919 | 21.3943 | -0.99484 | 14.5051 |  | -1.3946 | 14.9789 | -0.69652 | 10.1555 |  | -0.97981 | 10.5239 | -0.48936 | 7.1351 |  | -0.67499 | 7.2499 | -0.33712 | 4.9153 |  | -0.44151 | 4.7422 | -0.22051 | 3.2151 |  | -0.25696 | 2.76 | -0.12834 | 1.8712 |  | -0.10741 | 1.1537 | -0.053647 | 0.78219 |  | 0.016229 | -0.17431 | 0.44549 | -6.4953 |  | 0.27698 | -2.975 | 7.6032 | -110.8572 |  | 0.45082 | -4.8421 | 12.375 | -180.4317 |  | 0.57499 | -6.1758 | 15.7834 | -230.1278 |  | 0.66811 | -7.176 | 18.3397 | -267.3999 |  | 0.74055 | -7.954 | 20.328 | -296.3893 |  | 0.79849 | -8.5764 | 21.9186 | -319.5808 |  | 0.8459 | -9.0856 | 23.22 | -338.5557 |  | 0.88541 | -9.51 | 24.3045 | -354.3681
| 1 | 4.8 | 7.625 | 36.6 | 0.0465 | 49.6 | -176 | 35.2919 | -179.4175 |  | -2.9793 | 32 | -1.488 | 22.2478 |  | -2.9793 | 32 | -1.488 | 22.2478 |  | -2.9793 | 32 | -1.488 | 22.2478 |  | -2.9793 | 32 | -1.488 | 22.2478 |  | -2.9793 | 32 | -1.488 | 22.2478 |  | -2.9793 | 32 | -1.488 | 22.2478 |  | -2.9793 | 32 | -1.488 | 22.2478 |  | -2.9793 | 32 | -1.488 | 22.2478 |  | -2.9789 | 31.9959 | -1.4878 | 22.2449 |  | -2.033 | 21.8361 | -1.0154 | 15.1814 |  | -1.4283 | 15.341 | -0.71336 | 10.6657 |  | -1.0084 | 10.8307 | -0.50363 | 7.53 |  | -0.69977 | 7.516 | -0.3495 | 5.2255 |  | -0.46339 | 4.9772 | -0.23144 | 3.4603 |  | -0.27655 | 2.9703 | -0.13812 | 2.0651 |  | -0.12514 | 1.3441 | -0.062501 | 0.93448 |  | 3.6361e-05 | -0.00039055 | 0.0013308 | -0.019898 |  | 0.26403 | -2.8359 | 9.6635 | -144.4829 |  | 0.44002 | -4.7262 | 16.1049 | -240.7916 |  | 0.56574 | -6.0764 | 20.7059 | -309.5835 |  | 0.66002 | -7.0891 | 24.1567 | -361.1774 |  | 0.73335 | -7.8767 | 26.8406 | -401.306 |  | 0.79201 | -8.5068 | 28.9877 | -433.4089 |  | 0.84001 | -9.0224 | 30.7445 | -459.6749 |  | 0.88001 | -9.452 | 32.2084 | -481.5632
| 2 | 4.8 | 7.625 | 36.6 | 0.0465 | 44.8 | -176 | 30.5074 | -179.0317 |  | -2.9761 | 31.966 | -1.4864 | 22.1763 |  | -2.976 | 31.9646 | -1.4864 | 22.1754 |  | -2.9759 | 31.9632 | -1.4863 | 22.1744 |  | -2.9757 | 31.9616 | -1.4862 | 22.1733 |  | -2.9756 | 31.9598 | -1.4861 | 22.1721 |  | -2.9754 | 31.9579 | -1.486 | 22.1707 |  | -2.9752 | 31.9558 | -1.4859 | 22.1693 |  | -2.975 | 31.9535 | -1.4858 | 22.1677 |  | -2.9744 | 31.9468 | -1.4855 | 22.163 |  | -2.0295 | 21.7978 | -1.0136 | 15.1222 |  | -1.4254 | 15.3096 | -0.7119 | 10.621 |  | -1.0059 | 10.8041 | -0.50239 | 7.4953 |  | -0.69762 | 7.493 | -0.34842 | 5.1982 |  | -0.4615 | 4.9568 | -0.23049 | 3.4388 |  | -0.27485 | 2.9521 | -0.13727 | 2.048 |  | -0.1236 | 1.3276 | -0.061734 | 0.92102 |  | 0.0014393 | -0.01546 | 0.05268 | -0.78594 |  | 0.26515 | -2.8479 | 9.7045 | -144.7851 |  | 0.44096 | -4.7362 | 16.1391 | -240.7845 |  | 0.56654 | -6.085 | 20.7352 | -309.3555 |  | 0.66072 | -7.0966 | 24.1823 | -360.7837 |  | 0.73397 | -7.8834 | 26.8634 | -400.7835 |  | 0.79258 | -8.5129 | 29.0083 | -432.7833 |  | 0.84052 | -9.0278 | 30.7632 | -458.9649 |  | 0.88048 | -9.457 | 32.2256 | -480.783
| 3 | 4.8 | 7.625 | 36.6 | 0.0465 | 40 | -176 | 25.7229 | -178.6458 |  | -2.973 | 31.932 | -1.4848 | 22.105 |  | -2.9727 | 31.9293 | -1.4847 | 22.1031 |  | -2.9725 | 31.9263 | -1.4846 | 22.1011 |  | -2.9722 | 31.9231 | -1.4844 | 22.0989 |  | -2.9718 | 31.9196 | -1.4843 | 22.0965 |  | -2.9715 | 31.9158 | -1.4841 | 22.0938 |  | -2.9711 | 31.9116 | -1.4839 | 22.0909 |  | -2.9707 | 31.907 | -1.4837 | 22.0877 |  | -2.9698 | 31.8977 | -1.4832 | 22.0813 |  | -2.0259 | 21.7596 | -1.0118 | 15.0631 |  | -1.4225 | 15.2782 | -0.71044 | 10.5764 |  | -1.0034 | 10.7775 | -0.50116 | 7.4608 |  | -0.69547 | 7.4699 | -0.34735 | 5.1711 |  | -0.4596 | 4.9365 | -0.22955 | 3.4173 |  | -0.27315 | 2.9339 | -0.13643 | 2.031 |  | -0.12207 | 1.3111 | -0.060967 | 0.90762 |  | 0.0028423 | -0.030528 | 0.10403 | -1.5487 |  | 0.26627 | -2.86 | 9.7456 | -145.0846 |  | 0.44189 | -4.7463 | 16.1734 | -240.7752 |  | 0.56734 | -6.0936 | 20.7646 | -309.1256 |  | 0.66142 | -7.1042 | 24.208 | -360.3884 |  | 0.7346 | -7.8901 | 26.8862 | -400.2595 |  | 0.79314 | -8.5189 | 29.0288 | -432.1563 |  | 0.84103 | -9.0333 | 30.7818 | -458.2538 |  | 0.88095 | -9.462 | 32.2427 | -480.0016
| 4 | 4.8 | 7.625 | 36.6 | 0.0465 | 35.2 | -176 | 20.9385 | -178.26 |  | -2.9698 | 31.898 | -1.4833 | 22.0338 |  | -2.9694 | 31.8939 | -1.4831 | 22.0309 |  | -2.969 | 31.8895 | -1.4829 | 22.0279 |  | -2.9686 | 31.8847 | -1.4826 | 22.0246 |  | -2.9681 | 31.8795 | -1.4824 | 22.021 |  | -2.9676 | 31.8737 | -1.4821 | 22.017 |  | -2.967 | 31.8674 | -1.4818 | 22.0127 |  | -2.9663 | 31.8605 | -1.4815 | 22.0079 |  | -2.9652 | 31.8486 | -1.481 | 21.9997 |  | -2.0223 | 21.7213 | -1.01 | 15.0041 |  | -1.4195 | 15.2469 | -0.70898 | 10.5319 |  | -1.001 | 10.751 | -0.49992 | 7.4263 |  | -0.69333 | 7.4468 | -0.34628 | 5.144 |  | -0.45771 | 4.9161 | -0.2286 | 3.3958 |  | -0.27146 | 2.9156 | -0.13558 | 2.014 |  | -0.12053 | 1.2946 | -0.060199 | 0.89426 |  | 0.0042453 | -0.045597 | 0.15538 | -2.3081 |  | 0.2674 | -2.872 | 9.7867 | -145.3814 |  | 0.44283 | -4.7563 | 16.2076 | -240.7636 |  | 0.56814 | -6.1022 | 20.7939 | -308.8938 |  | 0.66212 | -7.1117 | 24.2337 | -359.9914 |  | 0.73522 | -7.8968 | 26.9091 | -399.734 |  | 0.7937 | -8.5249 | 29.0494 | -431.5281 |  | 0.84154 | -9.0388 | 30.8005 | -457.5414 |  | 0.88142 | -9.4671 | 32.2598 | -479.2192
b22 | 5 | 4.8 | 7.625 | 36.6 | 0.0465 | 30.4 | -176 | 16.154 | -177.8741 | b22 | -2.9666 | 31.864 | -1.4817 | 21.9626 | b22 | -2.9661 | 31.8585 | -1.4814 | 21.9589 | b22 | -2.9656 | 31.8526 | -1.4811 | 21.9548 | b22 | -2.965 | 31.8462 | -1.4809 | 21.9504 | b22 | -2.9643 | 31.8393 | -1.4805 | 21.9456 | b22 | -2.9636 | 31.8316 | -1.4802 | 21.9403 | b22 | -2.9629 | 31.8232 | -1.4798 | 21.9346 | b22 | -2.962 | 31.814 | -1.4793 | 21.9282 | b22 | -2.9606 | 31.7995 | -1.4787 | 21.9182 | b22 | -2.0188 | 21.683 | -1.0083 | 14.9453 | b22 | -1.4166 | 15.2155 | -0.70752 | 10.4875 | b22 | -0.99848 | 10.7244 | -0.49868 | 7.3919 | b22 | -0.69118 | 7.4238 | -0.34521 | 5.1169 | b22 | -0.45581 | 4.8957 | -0.22765 | 3.3745 | b22 | -0.26976 | 2.8974 | -0.13473 | 1.9971 | b22 | -0.119 | 1.2781 | -0.059432 | 0.88096 | b22 | 0.0056483 | -0.060666 | 0.20673 | -3.0643 | b22 | 0.26852 | -2.8841 | 9.8278 | -145.6757 | b22 | 0.44377 | -4.7664 | 16.2418 | -240.7499 | b22 | 0.56894 | -6.1109 | 20.8233 | -308.6601 | b22 | 0.66282 | -7.1192 | 24.2594 | -359.5928 | b22 | 0.73584 | -7.9035 | 26.9319 | -399.207 | b22 | 0.79426 | -8.5309 | 29.0699 | -430.8985 | b22 | 0.84205 | -9.0443 | 30.8192 | -456.8278 | b22 | 0.88188 | -9.4721 | 32.2769 | -478.4356
| 6 | 4.8 | 7.625 | 36.6 | 0.0465 | 25.6 | -176 | 11.3695 | -177.4883 |  | -2.9635 | 31.8299 | -1.4801 | 21.8916 |  | -2.9628 | 31.8232 | -1.4798 | 21.8869 |  | -2.9622 | 31.8158 | -1.4794 | 21.8819 |  | -2.9614 | 31.8078 | -1.4791 | 21.8764 |  | -2.9606 | 31.7991 | -1.4787 | 21.8704 |  | -2.9597 | 31.7896 | -1.4782 | 21.8638 |  | -2.9587 | 31.7791 | -1.4777 | 21.8566 |  | -2.9577 | 31.7675 | -1.4772 | 21.8486 |  | -2.9561 | 31.7505 | -1.4764 | 21.8369 |  | -2.0152 | 21.6447 | -1.0065 | 14.8865 |  | -1.4137 | 15.1841 | -0.70606 | 10.4431 |  | -0.996 | 10.6978 | -0.49745 | 7.3576 |  | -0.68903 | 7.4007 | -0.34413 | 5.09 |  | -0.45391 | 4.8754 | -0.22671 | 3.3531 |  | -0.26806 | 2.8792 | -0.13388 | 1.9802 |  | -0.11746 | 1.2616 | -0.058665 | 0.8677 |  | 0.0070512 | -0.075735 | 0.25807 | -3.8171 |  | 0.26964 | -2.8961 | 9.8689 | -145.9673 |  | 0.4447 | -4.7764 | 16.276 | -240.734 |  | 0.56974 | -6.1195 | 20.8526 | -308.4246 |  | 0.66353 | -7.1268 | 24.285 | -359.1925 |  | 0.73647 | -7.9102 | 26.9547 | -398.6786 |  | 0.79482 | -8.537 | 29.0904 | -430.2676 |  | 0.84256 | -9.0498 | 30.8378 | -456.113 |  | 0.88235 | -9.4771 | 32.294 | -477.6509
| 7 | 4.8 | 7.625 | 36.6 | 0.0465 | 20.8 | -176 | 6.5851 | -177.1024 |  | -2.9603 | 31.7959 | -1.4785 | 21.8207 |  | -2.9596 | 31.7878 | -1.4781 | 21.8151 |  | -2.9587 | 31.779 | -1.4777 | 21.809 |  | -2.9578 | 31.7694 | -1.4773 | 21.8024 |  | -2.9569 | 31.7589 | -1.4768 | 21.7953 |  | -2.9558 | 31.7475 | -1.4763 | 21.7874 |  | -2.9546 | 31.7349 | -1.4757 | 21.7788 |  | -2.9533 | 31.721 | -1.475 | 21.7692 |  | -2.9515 | 31.7014 | -1.4741 | 21.7558 |  | -2.0116 | 21.6064 | -1.0047 | 14.8279 |  | -1.4108 | 15.1527 | -0.7046 | 10.3989 |  | -0.99353 | 10.6712 | -0.49621 | 7.3234 |  | -0.68689 | 7.3777 | -0.34306 | 5.0631 |  | -0.45202 | 4.855 | -0.22576 | 3.3319 |  | -0.26637 | 2.861 | -0.13303 | 1.9634 |  | -0.11592 | 1.2451 | -0.057898 | 0.85449 |  | 0.0084542 | -0.090804 | 0.30942 | -4.5666 |  | 0.27076 | -2.9082 | 9.9099 | -146.2562 |  | 0.44564 | -4.7865 | 16.3103 | -240.7159 |  | 0.57055 | -6.1281 | 20.882 | -308.1871 |  | 0.66423 | -7.1343 | 24.3107 | -358.7905 |  | 0.73709 | -7.9169 | 26.9775 | -398.1488 |  | 0.79538 | -8.543 | 29.111 | -429.6353 |  | 0.84307 | -9.0552 | 30.8565 | -455.3971 |  | 0.88282 | -9.4821 | 32.3111 | -476.8652
| 8 | 4.8 | 7.625 | 36.6 | 0.0465 | 16 | -176 | 1.8006 | -176.7166 |  | -2.9571 | 31.7619 | -1.4769 | 21.7498 |  | -2.9563 | 31.7524 | -1.4765 | 21.7433 |  | -2.9553 | 31.7421 | -1.476 | 21.7363 |  | -2.9543 | 31.7309 | -1.4755 | 21.7286 |  | -2.9531 | 31.7187 | -1.4749 | 21.7203 |  | -2.9519 | 31.7054 | -1.4743 | 21.7111 |  | -2.9505 | 31.6907 | -1.4736 | 21.701 |  | -2.949 | 31.6744 | -1.4729 | 21.6899 |  | -2.9469 | 31.6523 | -1.4718 | 21.6748 |  | -2.0081 | 21.5682 | -1.0029 | 14.7694 |  | -1.4079 | 15.1214 | -0.70314 | 10.3548 |  | -0.99105 | 10.6446 | -0.49498 | 7.2892 |  | -0.68474 | 7.3546 | -0.34199 | 5.0363 |  | -0.45012 | 4.8347 | -0.22481 | 3.3107 |  | -0.26467 | 2.8427 | -0.13219 | 1.9466 |  | -0.11439 | 1.2286 | -0.057131 | 0.84133 |  | 0.0098572 | -0.10587 | 0.36077 | -5.3129 |  | 0.27189 | -2.9203 | 9.951 | -146.5425 |  | 0.44657 | -4.7965 | 16.3445 | -240.6956 |  | 0.57135 | -6.1367 | 20.9113 | -307.9478 |  | 0.66493 | -7.1418 | 24.3364 | -358.387 |  | 0.73771 | -7.9236 | 27.0003 | -397.6174 |  | 0.79594 | -8.549 | 29.1315 | -429.0018 |  | 0.84358 | -9.0607 | 30.8752 | -454.6799 |  | 0.88329 | -9.4871 | 32.3283 | -476.0783
| 9 | 4.8 | 7.625 | 36.6 | 0.0465 | 11.2 | -176 | -2.9839 | -176.3308 |  | -2.954 | 31.7279 | -1.4753 | 21.6791 |  | -2.953 | 31.717 | -1.4748 | 21.6717 |  | -2.9519 | 31.7053 | -1.4743 | 21.6636 |  | -2.9507 | 31.6925 | -1.4737 | 21.6549 |  | -2.9494 | 31.6785 | -1.4731 | 21.6454 |  | -2.948 | 31.6633 | -1.4723 | 21.6349 |  | -2.9464 | 31.6465 | -1.4716 | 21.6235 |  | -2.9447 | 31.6279 | -1.4707 | 21.6108 |  | -2.9424 | 31.6032 | -1.4696 | 21.5939 |  | -2.0045 | 21.5299 | -1.0011 | 14.711 |  | -1.4049 | 15.09 | -0.70168 | 10.3107 |  | -0.98858 | 10.6181 | -0.49374 | 7.2551 |  | -0.68259 | 7.3316 | -0.34092 | 5.0095 |  | -0.44823 | 4.8143 | -0.22387 | 3.2895 |  | -0.26297 | 2.8245 | -0.13134 | 1.9299 |  | -0.11285 | 1.2121 | -0.056364 | 0.82822 |  | 0.01126 | -0.12094 | 0.41212 | -6.0558 |  | 0.27301 | -2.9323 | 9.9921 | -146.8262 |  | 0.44751 | -4.8066 | 16.3787 | -240.6731 |  | 0.57215 | -6.1453 | 20.9406 | -307.7066 |  | 0.66563 | -7.1494 | 24.3621 | -357.9817 |  | 0.73834 | -7.9303 | 27.0232 | -397.0846 |  | 0.7965 | -8.555 | 29.152 | -428.3669 |  | 0.84409 | -9.0662 | 30.8939 | -453.9615 |  | 0.88375 | -9.4922 | 32.3454 | -475.2904
| 10 | 4.8 | 7.625 | 36.6 | 0.0465 | 6.4 | -176 | -7.7683 | -175.9449 |  | -2.9508 | 31.6939 | -1.4738 | 21.6085 |  | -2.9497 | 31.6817 | -1.4732 | 21.6001 |  | -2.9484 | 31.6684 | -1.4726 | 21.5911 |  | -2.9471 | 31.6541 | -1.4719 | 21.5813 |  | -2.9456 | 31.6384 | -1.4712 | 21.5706 |  | -2.944 | 31.6212 | -1.4704 | 21.5589 |  | -2.9423 | 31.6023 | -1.4695 | 21.546 |  | -2.9403 | 31.5814 | -1.4685 | 21.5318 |  | -2.9378 | 31.5542 | -1.4673 | 21.5132 |  | -2.0009 | 21.4916 | -0.99936 | 14.6527 |  | -1.402 | 15.0586 | -0.70023 | 10.2668 |  | -0.9861 | 10.5915 | -0.4925 | 7.2211 |  | -0.68045 | 7.3085 | -0.33985 | 4.9828 |  | -0.44633 | 4.7939 | -0.22292 | 3.2684 |  | -0.26127 | 2.8063 | -0.13049 | 1.9133 |  | -0.11132 | 1.1956 | -0.055596 | 0.81516 |  | 0.012663 | -0.13601 | 0.46347 | -6.7954 |  | 0.27413 | -2.9444 | 10.0332 | -147.1072 |  | 0.44844 | -4.8166 | 16.413 | -240.6484 |  | 0.57295 | -6.1539 | 20.97 | -307.4635 |  | 0.66633 | -7.1569 | 24.3877 | -357.5748 |  | 0.73896 | -7.937 | 27.046 | -396.5503 |  | 0.79707 | -8.5611 | 29.1726 | -427.7307 |  | 0.8446 | -9.0717 | 30.9125 | -453.2419 |  | 0.88422 | -9.4972 | 32.3625 | -474.5013
|  | Am: 4234.5; As: 9.9433 |  |  |  | -156.3162 | 1189.4002 |  |  |  | -112.8161 | 1783.6603 |  |  |  | 13.2388 | 3567.2843 |  |  |  | 163.2678 | 5674.8785 |  |  |  | 341.2028 | 8143.0638 |  |  |  | 551.0581 | 11005.2488 |  |  |  | 796.8052 | 14294.6822 |  |  |  | 1084.2619 | 18062.869 |  |  |  | 1421.564 | 22375.8904 |  |  |  | 1645.2501 | 23552.1021 |  |  |  | 1843.9508 | 24492.836 |  |  |  | 2029.1188 | 25182.7851 |  |  |  | 2206.1352 | 25614.7577 |  |  |  | 2378.0799 | 25783.369 |  |  |  | 2546.4912 | 25685.8437 |  |  |  | 2712.2482 | 25321.9621 |  |  |  | 2883.9761 | 24575.8055 |  |  |  | 3425.0889 | 20394.614 |  |  |  | 3785.8307 | 17607.1529 |  |  |  | 4043.5035 | 15616.1093 |  |  |  | 4236.758 | 14122.8266 |  |  |  | 4387.0672 | 12961.3845 |  |  |  | 4507.3144 | 12032.2309 |  |  |  | 4605.6986 | 11272.0142 |  |  |  | 4687.6854 | 10638.5003

## P-M, SD (hidden)
| fy = | 60 | ksi |  |  |  | Angle = | 4.6106 | deg | [10 empty] | R E I N F O R C E M E N T
| f'm = | 3 | ksi | [16 empty] | BAR | DIAM | As
| Em = | 2700 | ksi, (TMS 1.8.2.2.1) |  |  |  | te = | t - | 0.375 | [10 empty] | # | in | in2
| Es = | 29000 | ksi, (TMS 1.8.2.1) |  |  |  | emu = | 0.0025 | [11 empty] | 3 | 0.375 | 0.11
| Lw = | 30 | ft, (within vertical control joints) |  |  |  | f = | 0.9 | [11 empty] | 4 | 0.5 | 0.2
[20 empty] | 5 | 0.625 | 0.31
| tw = | 8 | in | 2 | # | 6 | at each ends, with |  | 8 | in center to edge. | [9 empty] | 6 | 0.75 | 0.44
|  | Ash, Horizontal | 1 | # | 6 | @ | 16 | in o.c. | [11 empty] | 7 | 0.875 | 0.6
|  | Asv, Vertical | 1 | # | 6 | @ | 24 | in o.c. | [11 empty] | 8 | 1 | 0.79
[20 empty] | 9 | 1.128 | 1
|  |  |  | b11 = | 48 | in , | b12 = | 24 | in , | bf1 = | 80 | in ,(TMS 1.9.4.2.3) | [7 empty] | 10 | 1.27 | 1.27
| tf1 = | 12 | in , | 2 | # | 5 | @ | 48 | in o.c., Vertical | [10 empty] | 11 | 1.41 | 1.56
[20 empty] | 14 | 1.693 | 2.25
|  |  |  | b21 = | 36 | in , | b22 = | 48 | in , | bf2 = | 92 | in, (TMS 1.9.4.2.3) | [7 empty] | 18 | 2.257 | 4
| tf2 = | 8 | in , | 2 | # | 5 | @ | 48 | in o.c., Vertical
fPn
|  |  |  | C | fPn | fMn | -318.1867 | [6 empty] | P | M
|  | 1 | Pure T | 0 | -318.1867 | 0 | -536.94
|  | 2 |  | 1e-05 | -536.94 | -235.2836 | 1677.0932 | [6 empty] | -447.45 | -164.6985
|  | 3 |  | 24.8301 | 1677.0932 | 31850.8153 | 1981.8062 | [6 empty] | 1397.5776 | 22295.5707
|  | 4 |  | 49.6602 | 1981.8062 | 35719.2536 | 2421.863 | [6 empty] | 1651.5052 | 25003.4775
|  | 5 |  | 74.4903 | 2421.863 | 40543.8393 | 2726.805 | [6 empty] | 2018.2192 | 28380.6875
|  | 6 |  | 99.3204 | 2726.805 | 43285.5062 | 3166.816 |  |  | fPn | fMn |  |  | 2272.3375 | 30299.8543
|  | 7 |  | 124.1505 | 3166.816 | 46520.4205 | 3471.8037 |  |  | -536.94 | -235.2836 |  |  | 2639.0133 | 32564.2944
|  | 8 |  | 148.9806 | 3471.8037 | 48132.5048 | 3911.7951 |  |  | 360 | 12763.3047 |  |  | 2893.1697 | 33692.7533
|  | 9 |  | 173.8107 | 3911.7951 | 49778.1494 | 4219.493 |  |  | 1677.0932 | 31850.8153 |  |  | 3259.8293 | 34844.7046
|  | 10 | C = Cb | 198.6408 | 4219.493 | 50221.8856 | 4531.3107 | [6 empty] | 3516.2441 | 35155.3199
|  | 11 |  | 219.1889 | 4531.3107 | 50120.3623 | 4833.8299 | [6 empty] | 3776.0922 | 35084.2536
|  | 12 |  | 239.7369 | 4833.8299 | 49737.7509 | 5129.3215 | [6 empty] | 4028.1916 | 34816.4256
|  | 13 |  | 260.2849 | 5129.3215 | 49056.5175 | 5419.2565 |  |  | fPn | fMn |  |  | 4274.4346 | 34339.5623 |  | P | M
|  | 14 |  | 280.8329 | 5419.2565 | 48064.958 | 5704.8456 |  |  | 4729.0131 | 0 |  |  | 4516.0471 | 33645.4706 |  | 3940.8443 | 0
|  | 15 |  | 301.3809 | 5704.8456 | 46753.6013 | 5986.8444 |  |  | 4729.0131 | 50221.8856 |  |  | 4754.038 | 32727.5209 |  | 3940.8443 | 35155.3199
|  | 16 |  | 321.929 | 5986.8444 | 45116.6283 | 6265.9778 | [6 empty] | 4989.037 | 31581.6398
|  | 17 |  | 342.477 | 6265.9778 | 43148.0958 | 6541.182 | [6 empty] | 5221.6481 | 30203.6671
|  | 18 | C = d | 363.025 | 6541.182 | 40866.1828 | 9146.52 | [6 empty] | 5450.985 | 28606.328
|  | 19 |  | 771.4281 | 9146.52 | 6005.2054 | 9146.52 | [6 empty] | 7622.1 | 4203.6438
|  | 20 |  | 1179.8313 | 9146.52 | 6005.2054 | 9146.52 | [6 empty] | 7622.1 | 4203.6438
|  | 21 |  | 1588.2344 | 9146.52 | 6005.2054 | 9146.52 | [6 empty] | 7622.1 | 4203.6438
|  | 22 |  | 1996.6375 | 9146.52 | 6005.2054 | 9146.52 | [6 empty] | 7622.1 | 4203.6438
|  | 23 |  | 2405.0406 | 9146.52 | 6005.2054 | 9146.52 | [6 empty] | 7622.1 | 4203.6438
|  | 24 |  | 2813.4438 | 9146.52 | 6005.2054 | 9146.52 | [6 empty] | 7622.1 | 4203.6438
|  | 25 |  | 3221.8469 | 9146.52 | 6005.2054 | 9146.52 | [6 empty] | 7622.1 | 4203.6438
|  | 26 |  | 3630.25 | 9146.52 | 6005.2054 | [7 empty] | 7622.1 | 4203.6438
|  | 27 | Pure C |  | 2069.5566 | 50221.8856
[5 empty] | 2069.5566 | 0
[13 empty] | 2 |  |  |  |  | 3 |  |  |  |  | 4 |  |  |  |  | 5 |  |  |  |  | 6 |  |  |  |  | 7 |  |  |  |  | 8 |  |  |  |  | 9 |  |  |  |  | 10 |  |  |  |  | 11 |  |  |  |  | 12 |  |  |  |  | 13 |  |  |  |  | 14 |  |  |  |  | 15 |  |  |  |  | 16 |  |  |  |  | 17 |  |  |  |  | 18 |  |  |  |  | 19 |  |  |  |  | 20 |  |  |  |  | 21 |  |  |  |  | 22 |  |  |  |  | 23 |  |  |  |  | 24 |  |  |  |  | 25 |  |  |  |  | 26
[12 empty] | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in |  |  | d = | 363.015 | in
[7 empty] | Xc | Yc | X | Y |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in |  |  | Cb = | 198.6308 | in
[7 empty] | -52 | 180 | -37.3626 | 183.5975 |  | C = | 1e-05 | in |  |  | C = | 24.8301 | in |  |  | C = | 49.6602 | in |  |  | C = | 74.4903 | in |  |  | C = | 99.3204 | in |  |  | C = | 124.1505 | in |  |  | C = | 148.9806 | in |  |  | C = | 173.8107 | in |  |  | C = | 198.6408 | in |  |  | C = | 219.1889 | in |  |  | C = | 239.7369 | in |  |  | C = | 260.2849 | in |  |  | C = | 280.8329 | in |  |  | C = | 301.3809 | in |  |  | C = | 321.929 | in |  |  | C = | 342.477 | in |  |  | C = | 363.025 | in |  |  | C = | 771.4281 | in |  |  | C = | 1179.8313 | in |  |  | C = | 1588.2344 | in |  |  | C = | 1996.6375 | in |  |  | C = | 2405.0406 | in |  |  | C = | 2813.4438 | in |  |  | C = | 3221.8469 | in |  |  | C = | 3630.25 | in
[6 empty] | Corner | 28 | 180 | 42.3785 | 177.1668 | [8 empty] | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi
[7 empty] | -40 | -180 | -54.3397 | -176.2021 | [8 empty] | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi |  |  |  |  | ksi
[7 empty] | 52 | -180 | 37.3626 | -183.5975 |  | fPn = | -536.94 | kips |  |  | fPn = | 1677.0932 | kips |  |  | fPn = | 1981.8062 | kips |  |  | fPn = | 2421.863 | kips |  |  | fPn = | 2726.805 | kips |  |  | fPn = | 3166.816 | kips |  |  | fPn = | 3471.8037 | kips |  |  | fPn = | 3911.7951 | kips |  |  | fPn = | 4219.493 | kips |  |  | fPn = | 4531.3107 | kips |  |  | fPn = | 4833.8299 | kips |  |  | fPn = | 5129.3215 | kips |  |  | fPn = | 5419.2565 | kips |  |  | fPn = | 5704.8456 | kips |  |  | fPn = | 5986.8444 | kips |  |  | fPn = | 6265.9778 | kips |  |  | fPn = | 6541.182 | kips |  |  | fPn = | 9146.52 | kips |  |  | fPn = | 9146.52 | kips |  |  | fPn = | 9146.52 | kips |  |  | fPn = | 9146.52 | kips |  |  | fPn = | 9146.52 | kips |  |  | fPn = | 9146.52 | kips |  |  | fPn = | 9146.52 | kips |  |  | fPn = | 9146.52 | kips
[12 empty] | fMn = | -235.2836 | ft-k |  |  | fMn = | 31850.8153 | ft-k |  |  | fMn = | 35719.2536 | ft-k |  |  | fMn = | 40543.8393 | ft-k |  |  | fMn = | 43285.5062 | ft-k |  |  | fMn = | 46520.4205 | ft-k |  |  | fMn = | 48132.5048 | ft-k |  |  | fMn = | 49778.1494 | ft-k |  |  | fMn = | 50221.8856 | ft-k |  |  | fMn = | 50120.3623 | ft-k |  |  | fMn = | 49737.7509 | ft-k |  |  | fMn = | 49056.5175 | ft-k |  |  | fMn = | 48064.958 | ft-k |  |  | fMn = | 46753.6013 | ft-k |  |  | fMn = | 45116.6283 | ft-k |  |  | fMn = | 43148.0958 | ft-k |  |  | fMn = | 40866.1828 | ft-k |  |  | fMn = | 6005.2054 | ft-k |  |  | fMn = | 6005.2054 | ft-k |  |  | fMn = | 6005.2054 | ft-k |  |  | fMn = | 6005.2054 | ft-k |  |  | fMn = | 6005.2054 | ft-k |  |  | fMn = | 6005.2054 | ft-k |  |  | fMn = | 6005.2054 | ft-k |  |  | fMn = | 6005.2054 | ft-k
|  |  | b | h | Am | As | Xc | Yc | X | Y |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M |  | fm | fs | P | M
1 |  | 1 | 4.8 | 11.625 | 55.8 | 0.062 | -49.6 | 174 | -35.4526 | 177.424 |  | 0 | 60 | -3.72 | -55.0014 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517 |  | 2.4 | 0 | 133.92 | 1980.0517
2 |  | 2 | 4.8 | 11.625 | 55.8 | 0.062 | -44.8 | 174 | -30.6682 | 177.0381 |  | 0 | 60 | -3.72 | -54.8818 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456 |  | 2.4 | 0 | 133.92 | 1975.7456
3 |  | 3 | 4.8 | 11.625 | 55.8 | 0.062 | -40 | 174 | -25.8837 | 176.6523 |  | 0 | 60 | -3.72 | -54.7622 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396 |  | 2.4 | 0 | 133.92 | 1971.4396
4 |  | 4 | 4.8 | 11.625 | 55.8 | 0.062 | -35.2 | 174 | -21.0992 | 176.2665 |  | 0 | 60 | -3.72 | -54.6426 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336 |  | 2.4 | 0 | 133.92 | 1967.1336
5 | b11 | 5 | 4.8 | 11.625 | 55.8 | 0.062 | -30.4 | 174 | -16.3148 | 175.8806 | b11 | 0 | 60 | -3.72 | -54.523 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276 | b11 | 2.4 | 0 | 133.92 | 1962.8276
6 |  | 6 | 4.8 | 11.625 | 55.8 | 0.062 | -25.6 | 174 | -11.5303 | 175.4948 |  | 0 | 60 | -3.72 | -54.4034 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216 |  | 2.4 | 0 | 133.92 | 1958.5216
7 |  | 7 | 4.8 | 11.625 | 55.8 | 0.062 | -20.8 | 174 | -6.7458 | 175.1089 |  | 0 | 60 | -3.72 | -54.2838 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155 |  | 2.4 | 0 | 133.92 | 1954.2155
8 |  | 8 | 4.8 | 11.625 | 55.8 | 0.062 | -16 | 174 | -1.9614 | 174.7231 |  | 0 | 60 | -3.72 | -54.1642 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095 |  | 2.4 | 0 | 133.92 | 1949.9095
9 |  | 9 | 4.8 | 11.625 | 55.8 | 0.062 | -11.2 | 174 | 2.8231 | 174.3372 |  | 0 | 60 | -3.72 | -54.0445 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035 |  | 2.4 | 0 | 133.92 | 1945.6035
10 |  | 10 | 4.8 | 11.625 | 55.8 | 0.062 | -6.4 | 174 | 7.6076 | 173.9514 |  | 0 | 60 | -3.72 | -53.9249 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975 |  | 2.4 | 0 | 133.92 | 1941.2975
11 |  | 1 | 2.4 | 11.625 | 27.9 | 0.062 | 26.8 | 174 | 40.7001 | 171.2826 |  | 0 | 60 | -3.72 | -53.0976 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571 |  | 2.4 | 0 | 66.96 | 955.7571
12 |  | 2 | 2.4 | 11.625 | 27.9 | 0.062 | 24.4 | 174 | 38.3079 | 171.4756 |  | 0 | 60 | -3.72 | -53.1574 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336 |  | 2.4 | 0 | 66.96 | 956.8336
13 |  | 3 | 2.4 | 11.625 | 27.9 | 0.062 | 22 | 174 | 35.9157 | 171.6685 |  | 0 | 60 | -3.72 | -53.2172 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101 |  | 2.4 | 0 | 66.96 | 957.9101
14 |  | 4 | 2.4 | 11.625 | 27.9 | 0.062 | 19.6 | 174 | 33.5234 | 171.8614 |  | 0 | 60 | -3.72 | -53.277 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866 |  | 2.4 | 0 | 66.96 | 958.9866
15 | b12 | 5 | 2.4 | 11.625 | 27.9 | 0.062 | 17.2 | 174 | 31.1312 | 172.0543 | b12 | 0 | 60 | -3.72 | -53.3368 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631 | b12 | 2.4 | 0 | 66.96 | 960.0631
16 |  | 6 | 2.4 | 11.625 | 27.9 | 0.062 | 14.8 | 174 | 28.739 | 172.2472 |  | 0 | 60 | -3.72 | -53.3966 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396 |  | 2.4 | 0 | 66.96 | 961.1396
17 |  | 7 | 2.4 | 11.625 | 27.9 | 0.062 | 12.4 | 174 | 26.3467 | 172.4402 |  | 0 | 60 | -3.72 | -53.4565 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161 |  | 2.4 | 0 | 66.96 | 962.2161
18 |  | 8 | 2.4 | 11.625 | 27.9 | 0.062 | 10 | 174 | 23.9545 | 172.6331 |  | 0 | 60 | -3.72 | -53.5163 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926 |  | 2.4 | 0 | 66.96 | 963.2926
19 |  | 9 | 2.4 | 11.625 | 27.9 | 0.062 | 7.6 | 174 | 21.5623 | 172.826 |  | 0 | 60 | -3.72 | -53.5761 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691 |  | 2.4 | 0 | 66.96 | 964.3691
20 |  | 10 | 2.4 | 11.625 | 27.9 | 0.062 | 5.2 | 174 | 19.17 | 173.0189 |  | 0 | 60 | -3.72 | -53.6359 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456 |  | 2.4 | 0 | 66.96 | 965.4456
21 |  | 1 | 8 | 4 | 32 | 0.22 | 0 | 178 | 14.3084 | 177.424 |  | 0 | 60 | -13.2 | -195.1664 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135 |  | 2.4 | 0 | 76.8 | 1135.5135
22 |  | 2 | 8 | 4 | 32 | 0.22 | 0 | 174 | 13.9868 | 173.4369 |  | 0 | 60 | -13.2 | -190.7806 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963 |  | 2.4 | 0 | 76.8 | 1109.9963
23 | at | 3 | 8 | 4 | 32 | 0.22 | 0 | 170 | 13.6653 | 169.4499 | at | 0 | 60 | -13.2 | -186.3949 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792 | at | 2.4 | 0 | 76.8 | 1084.4792
24 |  | 4 | 8 | 4 | 32 | 0.22 | 0 | 166 | 13.3438 | 165.4628 |  | 0 | 60 | -13.2 | -182.0091 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962 |  | 2.4 | 0 | 76.8 | 1058.962
25 |  | 1 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 159.9 | 12.8534 | 159.3826 |  | 0 | 60 | -9.02 | -119.8026 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789 |  | 2.4 | 0 | 150.06 | 1993.0789
26 |  | 2 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 151.7 | 12.1943 | 151.2091 |  | 0 | 60 | -9.02 | -113.6588 |  | 0 | 22.069 | -3.3177 | -41.8056 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697 |  | 2.4 | 0 | 150.06 | 1890.8697
27 |  | 3 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 143.5 | 11.5351 | 143.0356 |  | 0 | 60 | -9.02 | -107.5151 |  | 0 | 45.9342 | -6.9054 | -82.3104 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605 |  | 2.4 | 0 | 150.06 | 1788.6605
28 |  | 4 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 135.3 | 10.876 | 134.8622 |  | 0 | 60 | -9.02 | -101.3714 |  | 0 | 60 | -9.02 | -101.3714 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513 |  | 2.4 | 0 | 150.06 | 1686.4513
29 |  | 5 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 127.1 | 10.2168 | 126.6887 |  | 0 | 60 | -9.02 | -95.2277 |  | 0 | 60 | -9.02 | -95.2277 |  | 0 | 10.5823 | -1.5909 | -16.7955 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422 |  | 2.4 | 0 | 150.06 | 1584.2422
30 |  | 6 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 118.9 | 9.5577 | 118.5152 |  | 0 | 60 | -9.02 | -89.084 |  | 0 | 60 | -9.02 | -89.084 |  | 0 | 22.515 | -3.3847 | -33.4287 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033 |  | 2.4 | 0 | 150.06 | 1482.033
31 |  | 7 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 110.7 | 8.8985 | 110.3418 |  | 0 | 60 | -9.02 | -82.9402 |  | 0 | 60 | -9.02 | -82.9402 |  | 0 | 34.4476 | -5.1786 | -47.6182 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238 |  | 2.4 | 0 | 150.06 | 1379.8238
32 |  | 8 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 102.5 | 8.2394 | 102.1683 |  | 0 | 60 | -9.02 | -76.7965 |  | 0 | 60 | -9.02 | -76.7965 |  | 0 | 46.3802 | -6.9725 | -59.3639 |  | 0 | 6.7535 | -1.0153 | -8.644 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147 |  | 2.4 | 0 | 150.06 | 1277.6147
33 |  | 9 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 94.3 | 7.5802 | 93.9948 |  | 0 | 60 | -9.02 | -70.6528 |  | 0 | 60 | -9.02 | -70.6528 |  | 0 | 58.3128 | -8.7664 | -68.666 |  | 0 | 14.7085 | -2.2112 | -17.32 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055 |  | 2.4 | 0 | 150.06 | 1175.4055
34 | wt | 10 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 86.1 | 6.9211 | 85.8214 | wt | 0 | 60 | -9.02 | -64.5091 | wt | 0 | 60 | -9.02 | -64.5091 | wt | 0 | 60 | -9.02 | -64.5091 | wt | 0 | 22.6636 | -3.4071 | -24.3668 | wt | 0 | 0 | 0 | 0 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963 | wt | 2.4 | 0 | 150.06 | 1073.1963
35 |  | 11 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 77.9 | 6.2619 | 77.6479 |  | 0 | 60 | -9.02 | -58.3653 |  | 0 | 60 | -9.02 | -58.3653 |  | 0 | 60 | -9.02 | -58.3653 |  | 0 | 30.6187 | -4.603 | -29.7845 |  | 0 | 4.839 | -0.72747 | -4.7072 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871 |  | 2.4 | 0 | 150.06 | 970.9871
36 |  | 12 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 69.7 | 5.6028 | 69.4744 |  | 0 | 60 | -9.02 | -52.2216 |  | 0 | 60 | -9.02 | -52.2216 |  | 0 | 60 | -9.02 | -52.2216 |  | 0 | 38.5738 | -5.7989 | -33.5731 |  | 0 | 10.8053 | -1.6244 | -9.4045 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778 |  | 2.4 | 0 | 150.06 | 868.778
37 |  | 13 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 61.5 | 4.9436 | 61.301 |  | 0 | 60 | -9.02 | -46.0779 |  | 0 | 60 | -9.02 | -46.0779 |  | 0 | 60 | -9.02 | -46.0779 |  | 0 | 46.5288 | -6.9948 | -35.7325 |  | 0 | 16.7716 | -2.5213 | -12.88 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688 |  | 2.4 | 0 | 150.06 | 766.5688
38 |  | 14 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 53.3 | 4.2845 | 53.1275 |  | 0 | 60 | -9.02 | -39.9342 |  | 0 | 60 | -9.02 | -39.9342 |  | 0 | 60 | -9.02 | -39.9342 |  | 0 | 54.4839 | -8.1907 | -36.2628 |  | 0 | 22.7379 | -3.4183 | -15.1337 |  | 0 | 3.6904 | -0.55478 | -2.4562 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596 |  | 2.4 | 0 | 150.06 | 664.3596
39 |  | 15 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 45.1 | 3.6253 | 44.9541 |  | 0 | 60 | -9.02 | -33.7905 |  | 0 | 60 | -9.02 | -33.7905 |  | 0 | 60 | -9.02 | -33.7905 |  | 0 | 60 | -9.02 | -33.7905 |  | 0 | 28.7042 | -4.3152 | -16.1655 |  | 0 | 8.4634 | -1.2723 | -4.7664 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504 |  | 2.4 | 0 | 150.06 | 562.1504
40 |  | 16 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 36.9 | 2.9662 | 36.7806 |  | 0 | 60 | -9.02 | -27.6467 |  | 0 | 60 | -9.02 | -27.6467 |  | 0 | 60 | -9.02 | -27.6467 |  | 0 | 60 | -9.02 | -27.6467 |  | 0 | 34.6706 | -5.2121 | -15.9755 |  | 0 | 13.2364 | -1.9899 | -6.0991 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413 |  | 2.4 | 0 | 150.06 | 459.9413
41 |  | 17 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 28.7 | 2.307 | 28.6071 |  | 0 | 60 | -9.02 | -21.503 |  | 0 | 60 | -9.02 | -21.503 |  | 0 | 60 | -9.02 | -21.503 |  | 0 | 60 | -9.02 | -21.503 |  | 0 | 40.6369 | -6.1091 | -14.5636 |  | 0 | 18.0095 | -2.7074 | -6.4543 |  | 0 | 2.9246 | -0.43966 | -1.0481 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321 |  | 2.4 | 0 | 150.06 | 357.7321
42 |  | 18 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 20.5 | 1.6479 | 20.4337 |  | 0 | 60 | -9.02 | -15.3593 |  | 0 | 60 | -9.02 | -15.3593 |  | 0 | 60 | -9.02 | -15.3593 |  | 0 | 60 | -9.02 | -15.3593 |  | 0 | 46.6032 | -7.006 | -11.9299 |  | 0 | 22.7825 | -3.425 | -5.8321 |  | 0 | 6.9021 | -1.0376 | -1.7669 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229 |  | 2.4 | 0 | 150.06 | 255.5229
43 |  | 19 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 12.3 | 0.98873 | 12.2602 |  | 0 | 60 | -9.02 | -9.2156 |  | 0 | 60 | -9.02 | -9.2156 |  | 0 | 60 | -9.02 | -9.2156 |  | 0 | 60 | -9.02 | -9.2156 |  | 0 | 52.5695 | -7.9029 | -8.0743 |  | 0 | 27.5556 | -4.1425 | -4.2323 |  | 0 | 10.8797 | -1.6356 | -1.671 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138 |  | 2.4 | 0 | 150.06 | 153.3138
44 |  | 20 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | 4.1 | 0.32958 | 4.0867 |  | 0 | 60 | -9.02 | -3.0719 |  | 0 | 60 | -9.02 | -3.0719 |  | 0 | 60 | -9.02 | -3.0719 |  | 0 | 60 | -9.02 | -3.0719 |  | 0 | 58.5358 | -8.7999 | -2.9969 |  | 0 | 32.3286 | -4.8601 | -1.6552 |  | 0 | 14.8572 | -2.2335 | -0.76065 |  | 0 | 2.3776 | -0.35743 | -0.12173 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046 |  | 2.4 | 0 | 150.06 | 51.1046
45 |  | 1 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -4.1 | -0.32958 | -4.0867 |  | 0 | 60 | -9.02 | 3.0719 |  | 0 | 60 | -9.02 | 3.0719 |  | 0 | 60 | -9.02 | 3.0719 |  | 0 | 60 | -9.02 | 3.0719 |  | 0 | 60 | -9.02 | 3.0719 |  | 0 | 37.1017 | -5.5776 | 1.8995 |  | 0 | 18.8347 | -2.8315 | 0.96429 |  | 0 | 5.7869 | -0.86997 | 0.29628 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046 |  | 2.4 | 0 | 150.06 | -51.1046
46 |  | 2 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -12.3 | -0.98873 | -12.2602 |  | 0 | 60 | -9.02 | 9.2156 |  | 0 | 60 | -9.02 | 9.2156 |  | 0 | 60 | -9.02 | 9.2156 |  | 0 | 60 | -9.02 | 9.2156 |  | 0 | 60 | -9.02 | 9.2156 |  | 0 | 41.8747 | -6.2952 | 6.4317 |  | 0 | 22.8123 | -3.4294 | 3.5038 |  | 0 | 9.1962 | -1.3825 | 1.4125 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138 |  | 2.4 | 0 | 150.06 | -153.3138
47 |  | 3 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -20.5 | -1.6479 | -20.4337 |  | 0 | 60 | -9.02 | 15.3593 |  | 0 | 60 | -9.02 | 15.3593 |  | 0 | 60 | -9.02 | 15.3593 |  | 0 | 60 | -9.02 | 15.3593 |  | 0 | 60 | -9.02 | 15.3593 |  | 0 | 46.6478 | -7.0127 | 11.9413 |  | 0 | 26.7898 | -4.0274 | 6.8579 |  | 0 | 12.6055 | -1.895 | 3.2269 |  | 0 | 1.9674 | -0.29576 | 0.50362 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229 |  | 2.4 | 0 | 150.06 | -255.5229
48 |  | 4 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -28.7 | -2.307 | -28.6071 |  | 0 | 60 | -9.02 | 21.503 |  | 0 | 60 | -9.02 | 21.503 |  | 0 | 60 | -9.02 | 21.503 |  | 0 | 60 | -9.02 | 21.503 |  | 0 | 60 | -9.02 | 21.503 |  | 0 | 51.4208 | -7.7303 | 18.4284 |  | 0 | 30.7673 | -4.6254 | 11.0265 |  | 0 | 16.0149 | -2.4076 | 5.7395 |  | 0 | 4.9505 | -0.74423 | 1.7742 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321 |  | 2.4 | 0 | 150.06 | -357.7321
49 |  | 5 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -36.9 | -2.9662 | -36.7806 |  | 0 | 60 | -9.02 | 27.6467 |  | 0 | 60 | -9.02 | 27.6467 |  | 0 | 60 | -9.02 | 27.6467 |  | 0 | 60 | -9.02 | 27.6467 |  | 0 | 60 | -9.02 | 27.6467 |  | 0 | 56.1939 | -8.4478 | 25.893 |  | 0 | 34.7449 | -5.2233 | 16.0097 |  | 0 | 19.4242 | -2.9201 | 8.9503 |  | 0 | 7.9337 | -1.1927 | 3.6557 |  | 0 | 0.39335 | -0.059134 | 0.18125 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413 |  | 2.4 | 0 | 150.06 | -459.9413
50 |  | 6 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -45.1 | -3.6253 | -44.9541 |  | 0 | 60 | -9.02 | 33.7905 |  | 0 | 60 | -9.02 | 33.7905 |  | 0 | 60 | -9.02 | 33.7905 |  | 0 | 60 | -9.02 | 33.7905 |  | 0 | 60 | -9.02 | 33.7905 |  | 0 | 60 | -9.02 | 33.7905 |  | 0 | 38.7224 | -5.8213 | 21.8075 |  | 0 | 22.8335 | -3.4326 | 12.8592 |  | 0 | 10.9168 | -1.6412 | 6.1481 |  | 0 | 3.0968 | -0.46556 | 1.7441 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504 |  | 2.4 | 0 | 150.06 | -562.1504
51 |  | 7 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -53.3 | -4.2845 | -53.1275 |  | 0 | 60 | -9.02 | 39.9342 |  | 0 | 60 | -9.02 | 39.9342 |  | 0 | 60 | -9.02 | 39.9342 |  | 0 | 60 | -9.02 | 39.9342 |  | 0 | 60 | -9.02 | 39.9342 |  | 0 | 60 | -9.02 | 39.9342 |  | 0 | 42.7 | -6.4192 | 28.4198 |  | 0 | 26.2428 | -3.9452 | 17.4664 |  | 0 | 13.9 | -2.0896 | 9.2514 |  | 0 | 5.8003 | -0.87198 | 3.8605 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596 |  | 2.4 | 0 | 150.06 | -664.3596
52 |  | 8 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -61.5 | -4.9436 | -61.301 |  | 0 | 60 | -9.02 | 46.0779 |  | 0 | 60 | -9.02 | 46.0779 |  | 0 | 60 | -9.02 | 46.0779 |  | 0 | 60 | -9.02 | 46.0779 |  | 0 | 60 | -9.02 | 46.0779 |  | 0 | 60 | -9.02 | 46.0779 |  | 0 | 46.6775 | -7.0172 | 35.8467 |  | 0 | 29.6521 | -4.4577 | 22.7718 |  | 0 | 16.8831 | -2.5381 | 12.9656 |  | 0 | 8.5038 | -1.2784 | 6.5306 |  | 0 | 1.5609 | -0.23466 | 1.1987 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -766.5688 |  | 2.4 | 0 | 150.06 | -766.5688 |  | 2.4 | 0 | 150.06 | -766.5688 |  | 2.4 | 0 | 150.06 | -766.5688 |  | 2.4 | 0 | 150.06 | -766.5688 |  | 2.4 | 0 | 150.06 | -766.5688 |  | 2.4 | 0 | 150.06 | -766.5688 |  | 2.4 | 0 | 150.06 | -766.5688 |  | 2.4 | 0 | 150.06 | -766.5688 |  | 2.4 | 0 | 150.06 | -766.5688 |  | 2.4 | 0 | 150.06 | -766.5688
53 |  | 9 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -69.7 | -5.6028 | -69.4744 |  | 0 | 60 | -9.02 | 52.2216 |  | 0 | 60 | -9.02 | 52.2216 |  | 0 | 60 | -9.02 | 52.2216 |  | 0 | 60 | -9.02 | 52.2216 |  | 0 | 60 | -9.02 | 52.2216 |  | 0 | 60 | -9.02 | 52.2216 |  | 0 | 50.655 | -7.6151 | 44.0881 |  | 0 | 33.0615 | -4.9702 | 28.7754 |  | 0 | 19.8663 | -2.9866 | 17.2908 |  | 0 | 11.2073 | -1.6848 | 9.7544 |  | 0 | 4.0327 | -0.60625 | 3.5099 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -868.778 |  | 2.4 | 0 | 150.06 | -868.778 |  | 2.4 | 0 | 150.06 | -868.778 |  | 2.4 | 0 | 150.06 | -868.778 |  | 2.4 | 0 | 150.06 | -868.778 |  | 2.4 | 0 | 150.06 | -868.778 |  | 2.4 | 0 | 150.06 | -868.778 |  | 2.4 | 0 | 150.06 | -868.778 |  | 2.4 | 0 | 150.06 | -868.778 |  | 2.4 | 0 | 150.06 | -868.778 |  | 2.4 | 0 | 150.06 | -868.778
54 | wb | 10 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -77.9 | -6.2619 | -77.6479 | wb | 0 | 60 | -9.02 | 58.3653 | wb | 0 | 60 | -9.02 | 58.3653 | wb | 0 | 60 | -9.02 | 58.3653 | wb | 0 | 60 | -9.02 | 58.3653 | wb | 0 | 60 | -9.02 | 58.3653 | wb | 0 | 60 | -9.02 | 58.3653 | wb | 0 | 54.6326 | -8.2131 | 53.1441 | wb | 0 | 36.4708 | -5.4828 | 35.4772 | wb | 0 | 22.8494 | -3.435 | 22.2269 | wb | 0 | 13.9108 | -2.0913 | 13.5318 | wb | 0 | 6.5045 | -0.97784 | 6.3273 | wb | 0 | 0.26754 | -0.04022 | 0.26025 | wb | 0 | 0 | 0 | 0 | wb | 0 | 0 | 0 | 0 | wb | 0 | 0 | 0 | 0 | wb | 2.4 | 0 | 150.06 | -970.9871 | wb | 2.4 | 0 | 150.06 | -970.9871 | wb | 2.4 | 0 | 150.06 | -970.9871 | wb | 2.4 | 0 | 150.06 | -970.9871 | wb | 2.4 | 0 | 150.06 | -970.9871 | wb | 2.4 | 0 | 150.06 | -970.9871 | wb | 2.4 | 0 | 150.06 | -970.9871 | wb | 2.4 | 0 | 150.06 | -970.9871 | wb | 2.4 | 0 | 150.06 | -970.9871 | wb | 2.4 | 0 | 150.06 | -970.9871
55 |  | 11 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -86.1 | -6.9211 | -85.8214 |  | 0 | 60 | -9.02 | 64.5091 |  | 0 | 60 | -9.02 | 64.5091 |  | 0 | 60 | -9.02 | 64.5091 |  | 0 | 60 | -9.02 | 64.5091 |  | 0 | 60 | -9.02 | 64.5091 |  | 0 | 60 | -9.02 | 64.5091 |  | 0 | 58.6101 | -8.8111 | 63.0147 |  | 0 | 39.8801 | -5.9953 | 42.8771 |  | 0 | 25.8326 | -3.8835 | 27.7739 |  | 0 | 16.6143 | -2.4977 | 17.8629 |  | 0 | 8.9763 | -1.3494 | 9.6508 |  | 0 | 2.5442 | -0.38248 | 2.7354 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -1073.1963 |  | 2.4 | 0 | 150.06 | -1073.1963 |  | 2.4 | 0 | 150.06 | -1073.1963 |  | 2.4 | 0 | 150.06 | -1073.1963 |  | 2.4 | 0 | 150.06 | -1073.1963 |  | 2.4 | 0 | 150.06 | -1073.1963 |  | 2.4 | 0 | 150.06 | -1073.1963 |  | 2.4 | 0 | 150.06 | -1073.1963 |  | 2.4 | 0 | 150.06 | -1073.1963 |  | 2.4 | 0 | 150.06 | -1073.1963
56 |  | 12 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -94.3 | -7.5802 | -93.9948 |  | 0 | 60 | -9.02 | 70.6528 |  | 0 | 60 | -9.02 | 70.6528 |  | 0 | 60 | -9.02 | 70.6528 |  | 0 | 60 | -9.02 | 70.6528 |  | 0 | 60 | -9.02 | 70.6528 |  | 0 | 60 | -9.02 | 70.6528 |  | 0 | 60 | -9.02 | 70.6528 |  | 0 | 43.2894 | -6.5078 | 50.9753 |  | 0 | 28.8157 | -4.332 | 33.9319 |  | 0 | 19.3178 | -2.9041 | 22.7476 |  | 0 | 11.448 | -1.721 | 13.4806 |  | 0 | 4.8208 | -0.72473 | 5.6767 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -1175.4055 |  | 2.4 | 0 | 150.06 | -1175.4055 |  | 2.4 | 0 | 150.06 | -1175.4055 |  | 2.4 | 0 | 150.06 | -1175.4055 |  | 2.4 | 0 | 150.06 | -1175.4055 |  | 2.4 | 0 | 150.06 | -1175.4055 |  | 2.4 | 0 | 150.06 | -1175.4055 |  | 2.4 | 0 | 150.06 | -1175.4055 |  | 2.4 | 0 | 150.06 | -1175.4055
57 |  | 13 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -102.5 | -8.2394 | -102.1683 |  | 0 | 60 | -9.02 | 76.7965 |  | 0 | 60 | -9.02 | 76.7965 |  | 0 | 60 | -9.02 | 76.7965 |  | 0 | 60 | -9.02 | 76.7965 |  | 0 | 60 | -9.02 | 76.7965 |  | 0 | 60 | -9.02 | 76.7965 |  | 0 | 60 | -9.02 | 76.7965 |  | 0 | 46.6987 | -7.0204 | 59.7717 |  | 0 | 31.7989 | -4.7804 | 40.7007 |  | 0 | 22.0213 | -3.3105 | 28.186 |  | 0 | 13.9198 | -2.0926 | 17.8166 |  | 0 | 7.0975 | -1.067 | 9.0843 |  | 0 | 1.2735 | -0.19145 | 1.63 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -1277.6147 |  | 2.4 | 0 | 150.06 | -1277.6147 |  | 2.4 | 0 | 150.06 | -1277.6147 |  | 2.4 | 0 | 150.06 | -1277.6147 |  | 2.4 | 0 | 150.06 | -1277.6147 |  | 2.4 | 0 | 150.06 | -1277.6147 |  | 2.4 | 0 | 150.06 | -1277.6147 |  | 2.4 | 0 | 150.06 | -1277.6147 |  | 2.4 | 0 | 150.06 | -1277.6147
58 |  | 14 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -110.7 | -8.8985 | -110.3418 |  | 0 | 60 | -9.02 | 82.9402 |  | 0 | 60 | -9.02 | 82.9402 |  | 0 | 60 | -9.02 | 82.9402 |  | 0 | 60 | -9.02 | 82.9402 |  | 0 | 60 | -9.02 | 82.9402 |  | 0 | 60 | -9.02 | 82.9402 |  | 0 | 60 | -9.02 | 82.9402 |  | 0 | 50.108 | -7.5329 | 69.2662 |  | 0 | 34.782 | -5.2289 | 48.0805 |  | 0 | 24.7248 | -3.717 | 34.178 |  | 0 | 16.3916 | -2.4642 | 22.6587 |  | 0 | 9.3741 | -1.4092 | 12.9582 |  | 0 | 3.3835 | -0.50866 | 4.6772 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -1379.8238 |  | 2.4 | 0 | 150.06 | -1379.8238 |  | 2.4 | 0 | 150.06 | -1379.8238 |  | 2.4 | 0 | 150.06 | -1379.8238 |  | 2.4 | 0 | 150.06 | -1379.8238 |  | 2.4 | 0 | 150.06 | -1379.8238 |  | 2.4 | 0 | 150.06 | -1379.8238 |  | 2.4 | 0 | 150.06 | -1379.8238
59 |  | 15 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -118.9 | -9.5577 | -118.5152 |  | 0 | 60 | -9.02 | 89.084 |  | 0 | 60 | -9.02 | 89.084 |  | 0 | 60 | -9.02 | 89.084 |  | 0 | 60 | -9.02 | 89.084 |  | 0 | 60 | -9.02 | 89.084 |  | 0 | 60 | -9.02 | 89.084 |  | 0 | 60 | -9.02 | 89.084 |  | 0 | 53.5174 | -8.0454 | 79.459 |  | 0 | 37.7652 | -5.6774 | 56.0712 |  | 0 | 27.4283 | -4.1234 | 40.7237 |  | 0 | 18.8634 | -2.8358 | 28.0071 |  | 0 | 11.6508 | -1.7515 | 17.2983 |  | 0 | 5.4936 | -0.82587 | 8.1565 |  | 0 | 0.17604 | -0.026464 | 0.26137 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -1482.033 |  | 2.4 | 0 | 150.06 | -1482.033 |  | 2.4 | 0 | 150.06 | -1482.033 |  | 2.4 | 0 | 150.06 | -1482.033 |  | 2.4 | 0 | 150.06 | -1482.033 |  | 2.4 | 0 | 150.06 | -1482.033 |  | 2.4 | 0 | 150.06 | -1482.033 |  | 2.4 | 0 | 150.06 | -1482.033
60 |  | 16 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -127.1 | -10.2168 | -126.6887 |  | 0 | 60 | -9.02 | 95.2277 |  | 0 | 60 | -9.02 | 95.2277 |  | 0 | 60 | -9.02 | 95.2277 |  | 0 | 60 | -9.02 | 95.2277 |  | 0 | 60 | -9.02 | 95.2277 |  | 0 | 60 | -9.02 | 95.2277 |  | 0 | 60 | -9.02 | 95.2277 |  | 0 | 56.9267 | -8.558 | 90.3499 |  | 0 | 40.7484 | -6.1258 | 64.6728 |  | 0 | 30.1318 | -4.5298 | 47.823 |  | 0 | 21.3352 | -3.2074 | 33.8616 |  | 0 | 13.9274 | -2.0938 | 22.1046 |  | 0 | 7.6037 | -1.1431 | 12.068 |  | 0 | 2.1422 | -0.32205 | 3.4 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -1584.2422 |  | 2.4 | 0 | 150.06 | -1584.2422 |  | 2.4 | 0 | 150.06 | -1584.2422 |  | 2.4 | 0 | 150.06 | -1584.2422 |  | 2.4 | 0 | 150.06 | -1584.2422 |  | 2.4 | 0 | 150.06 | -1584.2422 |  | 2.4 | 0 | 150.06 | -1584.2422 |  | 2.4 | 0 | 150.06 | -1584.2422
61 |  | 17 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -135.3 | -10.876 | -134.8622 |  | 0 | 60 | -9.02 | 101.3714 |  | 0 | 60 | -9.02 | 101.3714 |  | 0 | 60 | -9.02 | 101.3714 |  | 0 | 60 | -9.02 | 101.3714 |  | 0 | 60 | -9.02 | 101.3714 |  | 0 | 60 | -9.02 | 101.3714 |  | 0 | 60 | -9.02 | 101.3714 |  | 0 | 60 | -9.02 | 101.3714 |  | 0 | 43.7315 | -6.5743 | 73.8854 |  | 0 | 32.8353 | -4.9362 | 55.476 |  | 0 | 23.8069 | -3.579 | 40.2224 |  | 0 | 16.204 | -2.436 | 27.3771 |  | 0 | 9.7137 | -1.4603 | 16.4116 |  | 0 | 4.1084 | -0.61764 | 6.9413 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -1686.4513 |  | 2.4 | 0 | 150.06 | -1686.4513 |  | 2.4 | 0 | 150.06 | -1686.4513 |  | 2.4 | 0 | 150.06 | -1686.4513 |  | 2.4 | 0 | 150.06 | -1686.4513 |  | 2.4 | 0 | 150.06 | -1686.4513 |  | 2.4 | 0 | 150.06 | -1686.4513 |  | 2.4 | 0 | 150.06 | -1686.4513
62 |  | 18 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -143.5 | -11.5351 | -143.0356 |  | 0 | 60 | -9.02 | 107.5151 |  | 0 | 60 | -9.02 | 107.5151 |  | 0 | 60 | -9.02 | 107.5151 |  | 0 | 60 | -9.02 | 107.5151 |  | 0 | 60 | -9.02 | 107.5151 |  | 0 | 60 | -9.02 | 107.5151 |  | 0 | 60 | -9.02 | 107.5151 |  | 0 | 60 | -9.02 | 107.5151 |  | 0 | 46.7147 | -7.0228 | 83.7089 |  | 0 | 35.5388 | -5.3427 | 63.6826 |  | 0 | 26.2787 | -3.9506 | 47.0893 |  | 0 | 18.4807 | -2.7783 | 33.1159 |  | 0 | 11.8238 | -1.7775 | 21.1873 |  | 0 | 6.0746 | -0.91322 | 10.8853 |  | 0 | 1.0594 | -0.15926 | 1.8984 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -1788.6605 |  | 2.4 | 0 | 150.06 | -1788.6605 |  | 2.4 | 0 | 150.06 | -1788.6605 |  | 2.4 | 0 | 150.06 | -1788.6605 |  | 2.4 | 0 | 150.06 | -1788.6605 |  | 2.4 | 0 | 150.06 | -1788.6605 |  | 2.4 | 0 | 150.06 | -1788.6605 |  | 2.4 | 0 | 150.06 | -1788.6605
63 |  | 19 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -151.7 | -12.1943 | -151.2091 |  | 0 | 60 | -9.02 | 113.6588 |  | 0 | 60 | -9.02 | 113.6588 |  | 0 | 60 | -9.02 | 113.6588 |  | 0 | 60 | -9.02 | 113.6588 |  | 0 | 60 | -9.02 | 113.6588 |  | 0 | 60 | -9.02 | 113.6588 |  | 0 | 60 | -9.02 | 113.6588 |  | 0 | 60 | -9.02 | 113.6588 |  | 0 | 49.6978 | -7.4712 | 94.1433 |  | 0 | 38.2423 | -5.7491 | 72.4429 |  | 0 | 28.7505 | -4.3222 | 54.4625 |  | 0 | 20.7573 | -3.1205 | 39.3209 |  | 0 | 13.9339 | -2.0947 | 26.3951 |  | 0 | 8.0408 | -1.2088 | 15.2319 |  | 0 | 2.9001 | -0.43598 | 5.4937 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -1890.8697 |  | 2.4 | 0 | 150.06 | -1890.8697 |  | 2.4 | 0 | 150.06 | -1890.8697 |  | 2.4 | 0 | 150.06 | -1890.8697 |  | 2.4 | 0 | 150.06 | -1890.8697 |  | 2.4 | 0 | 150.06 | -1890.8697 |  | 2.4 | 0 | 150.06 | -1890.8697 |  | 2.4 | 0 | 150.06 | -1890.8697
64 |  | 20 | 7.625 | 8.2 | 62.525 | 0.15033 | 0 | -159.9 | -12.8534 | -159.3826 |  | 0 | 60 | -9.02 | 119.8026 |  | 0 | 60 | -9.02 | 119.8026 |  | 0 | 60 | -9.02 | 119.8026 |  | 0 | 60 | -9.02 | 119.8026 |  | 0 | 60 | -9.02 | 119.8026 |  | 0 | 60 | -9.02 | 119.8026 |  | 0 | 60 | -9.02 | 119.8026 |  | 0 | 60 | -9.02 | 119.8026 |  | 0 | 52.681 | -7.9197 | 105.1886 |  | 0 | 40.9458 | -6.1555 | 81.7568 |  | 0 | 31.2223 | -4.6937 | 62.3418 |  | 0 | 23.034 | -3.4628 | 45.9922 |  | 0 | 16.0439 | -2.4119 | 32.0351 |  | 0 | 10.0071 | -1.5044 | 19.9812 |  | 0 | 4.7408 | -0.7127 | 9.466 |  | 0 | 0.1065 | -0.01601 | 0.21264 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 150.06 | -1993.0789 |  | 2.4 | 0 | 150.06 | -1993.0789 |  | 2.4 | 0 | 150.06 | -1993.0789 |  | 2.4 | 0 | 150.06 | -1993.0789 |  | 2.4 | 0 | 150.06 | -1993.0789 |  | 2.4 | 0 | 150.06 | -1993.0789 |  | 2.4 | 0 | 150.06 | -1993.0789 |  | 2.4 | 0 | 150.06 | -1993.0789
65 |  | 1 | 8 | 4 | 32 | 0.22 | 0 | -166 | -13.3438 | -165.4628 |  | 0 | 60 | -13.2 | 182.0091 |  | 0 | 60 | -13.2 | 182.0091 |  | 0 | 60 | -13.2 | 182.0091 |  | 0 | 60 | -13.2 | 182.0091 |  | 0 | 60 | -13.2 | 182.0091 |  | 0 | 60 | -13.2 | 182.0091 |  | 0 | 60 | -13.2 | 182.0091 |  | 0 | 60 | -13.2 | 182.0091 |  | 0 | 54.9001 | -12.078 | 166.5388 |  | 0 | 42.9569 | -9.4505 | 130.3092 |  | 0 | 33.061 | -7.2734 | 100.2901 |  | 0 | 24.7276 | -5.4401 | 75.0107 |  | 0 | 17.6136 | -3.875 | 53.4307 |  | 0 | 11.4697 | -2.5233 | 34.7932 |  | 0 | 6.1101 | -1.3442 | 18.5349 |  | 0 | 1.3936 | -0.3066 | 4.2276 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 76.8 | -1058.962 |  | 2.4 | 0 | 76.8 | -1058.962 |  | 2.4 | 0 | 76.8 | -1058.962 |  | 2.4 | 0 | 76.8 | -1058.962 |  | 2.4 | 0 | 76.8 | -1058.962 |  | 2.4 | 0 | 76.8 | -1058.962 |  | 2.4 | 0 | 76.8 | -1058.962 |  | 2.4 | 0 | 76.8 | -1058.962
66 |  | 2 | 8 | 4 | 32 | 0.22 | 0 | -170 | -13.6653 | -169.4499 |  | 0 | 60 | -13.2 | 186.3949 |  | 0 | 60 | -13.2 | 186.3949 |  | 0 | 60 | -13.2 | 186.3949 |  | 0 | 60 | -13.2 | 186.3949 |  | 0 | 60 | -13.2 | 186.3949 |  | 0 | 60 | -13.2 | 186.3949 |  | 0 | 60 | -13.2 | 186.3949 |  | 0 | 60 | -13.2 | 186.3949 |  | 0 | 56.3553 | -12.3982 | 175.0724 |  | 0 | 44.2757 | -9.7407 | 137.5461 |  | 0 | 34.2668 | -7.5387 | 106.4525 |  | 0 | 25.8381 | -5.6844 | 80.2683 |  | 0 | 18.6429 | -4.1014 | 57.9158 |  | 0 | 12.4288 | -2.7343 | 38.6112 |  | 0 | 7.008 | -1.5418 | 21.771 |  | 0 | 2.2377 | -0.49229 | 6.9515 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 76.8 | -1084.4792 |  | 2.4 | 0 | 76.8 | -1084.4792 |  | 2.4 | 0 | 76.8 | -1084.4792 |  | 2.4 | 0 | 76.8 | -1084.4792 |  | 2.4 | 0 | 76.8 | -1084.4792 |  | 2.4 | 0 | 76.8 | -1084.4792 |  | 2.4 | 0 | 76.8 | -1084.4792 |  | 2.4 | 0 | 76.8 | -1084.4792
67 | ab | 3 | 8 | 4 | 32 | 0.22 | 0 | -174 | -13.9868 | -173.4369 | ab | 0 | 60 | -13.2 | 190.7806 | ab | 0 | 60 | -13.2 | 190.7806 | ab | 0 | 60 | -13.2 | 190.7806 | ab | 0 | 60 | -13.2 | 190.7806 | ab | 0 | 60 | -13.2 | 190.7806 | ab | 0 | 60 | -13.2 | 190.7806 | ab | 0 | 60 | -13.2 | 190.7806 | ab | 0 | 60 | -13.2 | 190.7806 | ab | 0 | 57.8105 | -12.7183 | 183.8188 | ab | 0 | 45.5945 | -10.0308 | 144.9757 | ab | 0 | 35.4725 | -7.804 | 112.7911 | ab | 0 | 26.9487 | -5.9287 | 85.6882 | ab | 0 | 19.6722 | -4.3279 | 62.5513 | ab | 0 | 13.388 | -2.9454 | 42.5694 | ab | 0 | 7.9059 | -1.7393 | 25.1383 | ab | 0 | 3.0817 | -0.67798 | 9.7988 | ab | 0 | 0 | 0 | 0 | ab | 2.4 | 0 | 76.8 | -1109.9963 | ab | 2.4 | 0 | 76.8 | -1109.9963 | ab | 2.4 | 0 | 76.8 | -1109.9963 | ab | 2.4 | 0 | 76.8 | -1109.9963 | ab | 2.4 | 0 | 76.8 | -1109.9963 | ab | 2.4 | 0 | 76.8 | -1109.9963 | ab | 2.4 | 0 | 76.8 | -1109.9963 | ab | 2.4 | 0 | 76.8 | -1109.9963
68 |  | 4 | 8 | 4 | 32 | 0.22 | 0 | -178 | -14.3084 | -177.424 |  | 0 | 60 | -13.2 | 195.1664 |  | 0 | 60 | -13.2 | 195.1664 |  | 0 | 60 | -13.2 | 195.1664 |  | 0 | 60 | -13.2 | 195.1664 |  | 0 | 60 | -13.2 | 195.1664 |  | 0 | 60 | -13.2 | 195.1664 |  | 0 | 60 | -13.2 | 195.1664 |  | 0 | 60 | -13.2 | 195.1664 |  | 0 | 59.2657 | -13.0385 | 192.778 |  | 0 | 46.9133 | -10.3209 | 152.5982 |  | 0 | 36.6783 | -8.0692 | 119.3061 |  | 0 | 28.0593 | -6.173 | 91.2704 |  | 0 | 20.7015 | -4.5543 | 67.3374 |  | 0 | 14.3471 | -3.1564 | 46.6678 |  | 0 | 8.8038 | -1.9368 | 28.6369 |  | 0 | 3.9257 | -0.86366 | 12.7695 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 76.8 | -1135.5135 |  | 2.4 | 0 | 76.8 | -1135.5135 |  | 2.4 | 0 | 76.8 | -1135.5135 |  | 2.4 | 0 | 76.8 | -1135.5135 |  | 2.4 | 0 | 76.8 | -1135.5135 |  | 2.4 | 0 | 76.8 | -1135.5135 |  | 2.4 | 0 | 76.8 | -1135.5135 |  | 2.4 | 0 | 76.8 | -1135.5135
69 |  | 1 | 3.6 | 7.625 | 27.45 | 0.0465 | -38.2 | -176 | -52.224 | -172.3598 |  | 0 | 60 | -2.79 | 40.0736 |  | 0 | 60 | -2.79 | 40.0736 |  | 0 | 60 | -2.79 | 40.0736 |  | 0 | 60 | -2.79 | 40.0736 |  | 0 | 60 | -2.79 | 40.0736 |  | 0 | 60 | -2.79 | 40.0736 |  | 0 | 60 | -2.79 | 40.0736 |  | 0 | 60 | -2.79 | 40.0736 |  | 0 | 57.4174 | -2.6699 | 38.3487 |  | 0 | 45.2382 | -2.1036 | 30.2143 |  | 0 | 35.1468 | -1.6343 | 23.4743 |  | 0 | 26.6487 | -1.2392 | 17.7985 |  | 0 | 19.3941 | -0.90183 | 12.9532 |  | 0 | 13.1288 | -0.61049 | 8.7687 |  | 0 | 7.6633 | -0.35635 | 5.1183 |  | 0 | 2.8537 | -0.1327 | 1.906 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 65.88 | -946.2552 |  | 2.4 | 0 | 65.88 | -946.2552 |  | 2.4 | 0 | 65.88 | -946.2552 |  | 2.4 | 0 | 65.88 | -946.2552 |  | 2.4 | 0 | 65.88 | -946.2552 |  | 2.4 | 0 | 65.88 | -946.2552 |  | 2.4 | 0 | 65.88 | -946.2552 |  | 2.4 | 0 | 65.88 | -946.2552
70 |  | 2 | 3.6 | 7.625 | 27.45 | 0.0465 | -34.6 | -176 | -48.6357 | -172.6492 |  | 0 | 60 | -2.79 | 40.1409 |  | 0 | 60 | -2.79 | 40.1409 |  | 0 | 60 | -2.79 | 40.1409 |  | 0 | 60 | -2.79 | 40.1409 |  | 0 | 60 | -2.79 | 40.1409 |  | 0 | 60 | -2.79 | 40.1409 |  | 0 | 60 | -2.79 | 40.1409 |  | 0 | 60 | -2.79 | 40.1409 |  | 0 | 57.523 | -2.6748 | 38.4838 |  | 0 | 45.3339 | -2.108 | 30.3291 |  | 0 | 35.2343 | -1.6384 | 23.5723 |  | 0 | 26.7293 | -1.2429 | 17.8823 |  | 0 | 19.4689 | -0.9053 | 13.025 |  | 0 | 13.1985 | -0.61373 | 8.83 |  | 0 | 7.7285 | -0.35938 | 5.1705 |  | 0 | 2.9149 | -0.13554 | 1.9501 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 65.88 | -947.8439 |  | 2.4 | 0 | 65.88 | -947.8439 |  | 2.4 | 0 | 65.88 | -947.8439 |  | 2.4 | 0 | 65.88 | -947.8439 |  | 2.4 | 0 | 65.88 | -947.8439 |  | 2.4 | 0 | 65.88 | -947.8439 |  | 2.4 | 0 | 65.88 | -947.8439 |  | 2.4 | 0 | 65.88 | -947.8439
71 |  | 3 | 3.6 | 7.625 | 27.45 | 0.0465 | -31 | -176 | -45.0473 | -172.9385 |  | 0 | 60 | -2.79 | 40.2082 |  | 0 | 60 | -2.79 | 40.2082 |  | 0 | 60 | -2.79 | 40.2082 |  | 0 | 60 | -2.79 | 40.2082 |  | 0 | 60 | -2.79 | 40.2082 |  | 0 | 60 | -2.79 | 40.2082 |  | 0 | 60 | -2.79 | 40.2082 |  | 0 | 60 | -2.79 | 40.2082 |  | 0 | 57.6286 | -2.6797 | 38.6191 |  | 0 | 45.4296 | -2.1125 | 30.4441 |  | 0 | 35.3218 | -1.6425 | 23.6704 |  | 0 | 26.8099 | -1.2467 | 17.9663 |  | 0 | 19.5436 | -0.90878 | 13.0969 |  | 0 | 13.2681 | -0.61697 | 8.8914 |  | 0 | 7.7937 | -0.36241 | 5.2228 |  | 0 | 2.9762 | -0.13839 | 1.9945 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 65.88 | -949.4326 |  | 2.4 | 0 | 65.88 | -949.4326 |  | 2.4 | 0 | 65.88 | -949.4326 |  | 2.4 | 0 | 65.88 | -949.4326 |  | 2.4 | 0 | 65.88 | -949.4326 |  | 2.4 | 0 | 65.88 | -949.4326 |  | 2.4 | 0 | 65.88 | -949.4326 |  | 2.4 | 0 | 65.88 | -949.4326
72 |  | 4 | 3.6 | 7.625 | 27.45 | 0.0465 | -27.4 | -176 | -41.4589 | -173.2279 |  | 0 | 60 | -2.79 | 40.2755 |  | 0 | 60 | -2.79 | 40.2755 |  | 0 | 60 | -2.79 | 40.2755 |  | 0 | 60 | -2.79 | 40.2755 |  | 0 | 60 | -2.79 | 40.2755 |  | 0 | 60 | -2.79 | 40.2755 |  | 0 | 60 | -2.79 | 40.2755 |  | 0 | 60 | -2.79 | 40.2755 |  | 0 | 57.7343 | -2.6846 | 38.7546 |  | 0 | 45.5253 | -2.1169 | 30.5593 |  | 0 | 35.4093 | -1.6465 | 23.7688 |  | 0 | 26.8905 | -1.2504 | 18.0505 |  | 0 | 19.6183 | -0.91225 | 13.1689 |  | 0 | 13.3377 | -0.6202 | 8.953 |  | 0 | 7.8589 | -0.36544 | 5.2753 |  | 0 | 3.0375 | -0.14124 | 2.0389 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 65.88 | -951.0213 |  | 2.4 | 0 | 65.88 | -951.0213 |  | 2.4 | 0 | 65.88 | -951.0213 |  | 2.4 | 0 | 65.88 | -951.0213 |  | 2.4 | 0 | 65.88 | -951.0213 |  | 2.4 | 0 | 65.88 | -951.0213 |  | 2.4 | 0 | 65.88 | -951.0213 |  | 2.4 | 0 | 65.88 | -951.0213
73 | b21 | 5 | 3.6 | 7.625 | 27.45 | 0.0465 | -23.8 | -176 | -37.8706 | -173.5173 | b21 | 0 | 60 | -2.79 | 40.3428 | b21 | 0 | 60 | -2.79 | 40.3428 | b21 | 0 | 60 | -2.79 | 40.3428 | b21 | 0 | 60 | -2.79 | 40.3428 | b21 | 0 | 60 | -2.79 | 40.3428 | b21 | 0 | 60 | -2.79 | 40.3428 | b21 | 0 | 60 | -2.79 | 40.3428 | b21 | 0 | 60 | -2.79 | 40.3428 | b21 | 0 | 57.8399 | -2.6896 | 38.8903 | b21 | 0 | 45.6211 | -2.1214 | 30.6747 | b21 | 0 | 35.4968 | -1.6506 | 23.8673 | b21 | 0 | 26.9711 | -1.2542 | 18.1348 | b21 | 0 | 19.693 | -0.91572 | 13.2412 | b21 | 0 | 13.4073 | -0.62344 | 9.0148 | b21 | 0 | 7.924 | -0.36847 | 5.328 | b21 | 0 | 3.0987 | -0.14409 | 2.0835 | b21 | 0 | 0 | 0 | 0 | b21 | 2.4 | 0 | 65.88 | -952.61 | b21 | 2.4 | 0 | 65.88 | -952.61 | b21 | 2.4 | 0 | 65.88 | -952.61 | b21 | 2.4 | 0 | 65.88 | -952.61 | b21 | 2.4 | 0 | 65.88 | -952.61 | b21 | 2.4 | 0 | 65.88 | -952.61 | b21 | 2.4 | 0 | 65.88 | -952.61 | b21 | 2.4 | 0 | 65.88 | -952.61
74 |  | 6 | 3.6 | 7.625 | 27.45 | 0.0465 | -20.2 | -176 | -34.2822 | -173.8067 |  | 0 | 60 | -2.79 | 40.4101 |  | 0 | 60 | -2.79 | 40.4101 |  | 0 | 60 | -2.79 | 40.4101 |  | 0 | 60 | -2.79 | 40.4101 |  | 0 | 60 | -2.79 | 40.4101 |  | 0 | 60 | -2.79 | 40.4101 |  | 0 | 60 | -2.79 | 40.4101 |  | 0 | 60 | -2.79 | 40.4101 |  | 0 | 57.9455 | -2.6945 | 39.0263 |  | 0 | 45.7168 | -2.1258 | 30.7903 |  | 0 | 35.5843 | -1.6547 | 23.9661 |  | 0 | 27.0517 | -1.2579 | 18.2193 |  | 0 | 19.7677 | -0.9192 | 13.3136 |  | 0 | 13.4769 | -0.62668 | 9.0767 |  | 0 | 7.9892 | -0.3715 | 5.3807 |  | 0 | 3.16 | -0.14694 | 2.1283 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 65.88 | -954.1988 |  | 2.4 | 0 | 65.88 | -954.1988 |  | 2.4 | 0 | 65.88 | -954.1988 |  | 2.4 | 0 | 65.88 | -954.1988 |  | 2.4 | 0 | 65.88 | -954.1988 |  | 2.4 | 0 | 65.88 | -954.1988 |  | 2.4 | 0 | 65.88 | -954.1988 |  | 2.4 | 0 | 65.88 | -954.1988
75 |  | 7 | 3.6 | 7.625 | 27.45 | 0.0465 | -16.6 | -176 | -30.6939 | -174.0961 |  | 0 | 60 | -2.79 | 40.4773 |  | 0 | 60 | -2.79 | 40.4773 |  | 0 | 60 | -2.79 | 40.4773 |  | 0 | 60 | -2.79 | 40.4773 |  | 0 | 60 | -2.79 | 40.4773 |  | 0 | 60 | -2.79 | 40.4773 |  | 0 | 60 | -2.79 | 40.4773 |  | 0 | 60 | -2.79 | 40.4773 |  | 0 | 58.0511 | -2.6994 | 39.1626 |  | 0 | 45.8125 | -2.1303 | 30.9061 |  | 0 | 35.6719 | -1.6587 | 24.065 |  | 0 | 27.1323 | -1.2617 | 18.3041 |  | 0 | 19.8424 | -0.92267 | 13.3861 |  | 0 | 13.5465 | -0.62991 | 9.1388 |  | 0 | 8.0544 | -0.37453 | 5.4337 |  | 0 | 3.2212 | -0.14979 | 2.1731 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 65.88 | -955.7875 |  | 2.4 | 0 | 65.88 | -955.7875 |  | 2.4 | 0 | 65.88 | -955.7875 |  | 2.4 | 0 | 65.88 | -955.7875 |  | 2.4 | 0 | 65.88 | -955.7875 |  | 2.4 | 0 | 65.88 | -955.7875 |  | 2.4 | 0 | 65.88 | -955.7875 |  | 2.4 | 0 | 65.88 | -955.7875
76 |  | 8 | 3.6 | 7.625 | 27.45 | 0.0465 | -13 | -176 | -27.1055 | -174.3855 |  | 0 | 60 | -2.79 | 40.5446 |  | 0 | 60 | -2.79 | 40.5446 |  | 0 | 60 | -2.79 | 40.5446 |  | 0 | 60 | -2.79 | 40.5446 |  | 0 | 60 | -2.79 | 40.5446 |  | 0 | 60 | -2.79 | 40.5446 |  | 0 | 60 | -2.79 | 40.5446 |  | 0 | 60 | -2.79 | 40.5446 |  | 0 | 58.1567 | -2.7043 | 39.299 |  | 0 | 45.9082 | -2.1347 | 31.0222 |  | 0 | 35.7594 | -1.6628 | 24.1642 |  | 0 | 27.2129 | -1.2654 | 18.3889 |  | 0 | 19.9171 | -0.92615 | 13.4589 |  | 0 | 13.6161 | -0.63315 | 9.201 |  | 0 | 8.1195 | -0.37756 | 5.4867 |  | 0 | 3.2825 | -0.15264 | 2.2181 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 65.88 | -957.3762 |  | 2.4 | 0 | 65.88 | -957.3762 |  | 2.4 | 0 | 65.88 | -957.3762 |  | 2.4 | 0 | 65.88 | -957.3762 |  | 2.4 | 0 | 65.88 | -957.3762 |  | 2.4 | 0 | 65.88 | -957.3762 |  | 2.4 | 0 | 65.88 | -957.3762 |  | 2.4 | 0 | 65.88 | -957.3762
77 |  | 9 | 3.6 | 7.625 | 27.45 | 0.0465 | -9.4 | -176 | -23.5172 | -174.6748 |  | 0 | 60 | -2.79 | 40.6119 |  | 0 | 60 | -2.79 | 40.6119 |  | 0 | 60 | -2.79 | 40.6119 |  | 0 | 60 | -2.79 | 40.6119 |  | 0 | 60 | -2.79 | 40.6119 |  | 0 | 60 | -2.79 | 40.6119 |  | 0 | 60 | -2.79 | 40.6119 |  | 0 | 60 | -2.79 | 40.6119 |  | 0 | 58.2623 | -2.7092 | 39.4357 |  | 0 | 46.0039 | -2.1392 | 31.1385 |  | 0 | 35.8469 | -1.6669 | 24.2635 |  | 0 | 27.2935 | -1.2691 | 18.474 |  | 0 | 19.9918 | -0.92962 | 13.5318 |  | 0 | 13.6858 | -0.63639 | 9.2634 |  | 0 | 8.1847 | -0.38059 | 5.5399 |  | 0 | 3.3438 | -0.15549 | 2.2633 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 65.88 | -958.9649 |  | 2.4 | 0 | 65.88 | -958.9649 |  | 2.4 | 0 | 65.88 | -958.9649 |  | 2.4 | 0 | 65.88 | -958.9649 |  | 2.4 | 0 | 65.88 | -958.9649 |  | 2.4 | 0 | 65.88 | -958.9649 |  | 2.4 | 0 | 65.88 | -958.9649 |  | 2.4 | 0 | 65.88 | -958.9649
78 |  | 10 | 3.6 | 7.625 | 27.45 | 0.0465 | -5.8 | -176 | -19.9288 | -174.9642 |  | 0 | 60 | -2.79 | 40.6792 |  | 0 | 60 | -2.79 | 40.6792 |  | 0 | 60 | -2.79 | 40.6792 |  | 0 | 60 | -2.79 | 40.6792 |  | 0 | 60 | -2.79 | 40.6792 |  | 0 | 60 | -2.79 | 40.6792 |  | 0 | 60 | -2.79 | 40.6792 |  | 0 | 60 | -2.79 | 40.6792 |  | 0 | 58.368 | -2.7141 | 39.5727 |  | 0 | 46.0997 | -2.1436 | 31.2549 |  | 0 | 35.9344 | -1.6709 | 24.363 |  | 0 | 27.3741 | -1.2729 | 18.5593 |  | 0 | 20.0665 | -0.93309 | 13.6048 |  | 0 | 13.7554 | -0.63962 | 9.326 |  | 0 | 8.2499 | -0.38362 | 5.5933 |  | 0 | 3.405 | -0.15833 | 2.3086 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 65.88 | -960.5536 |  | 2.4 | 0 | 65.88 | -960.5536 |  | 2.4 | 0 | 65.88 | -960.5536 |  | 2.4 | 0 | 65.88 | -960.5536 |  | 2.4 | 0 | 65.88 | -960.5536 |  | 2.4 | 0 | 65.88 | -960.5536 |  | 2.4 | 0 | 65.88 | -960.5536 |  | 2.4 | 0 | 65.88 | -960.5536
79 |  | 1 | 4.8 | 7.625 | 36.6 | 0.0465 | 49.6 | -176 | 35.2919 | -179.4175 |  | 0 | 60 | -2.79 | 41.7146 |  | 0 | 60 | -2.79 | 41.7146 |  | 0 | 60 | -2.79 | 41.7146 |  | 0 | 60 | -2.79 | 41.7146 |  | 0 | 60 | -2.79 | 41.7146 |  | 0 | 60 | -2.79 | 41.7146 |  | 0 | 60 | -2.79 | 41.7146 |  | 0 | 60 | -2.79 | 41.7146 |  | 0 | 59.9933 | -2.7897 | 41.7099 |  | 0 | 47.5726 | -2.2121 | 33.0745 |  | 0 | 37.2811 | -1.7336 | 25.9194 |  | 0 | 28.6145 | -1.3306 | 19.8941 |  | 0 | 21.2162 | -0.98655 | 14.7504 |  | 0 | 14.8266 | -0.68944 | 10.3081 |  | 0 | 9.2528 | -0.43025 | 6.4329 |  | 0 | 4.3478 | -0.20217 | 3.0227 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 87.84 | -1313.3362 |  | 2.4 | 0 | 87.84 | -1313.3362 |  | 2.4 | 0 | 87.84 | -1313.3362 |  | 2.4 | 0 | 87.84 | -1313.3362 |  | 2.4 | 0 | 87.84 | -1313.3362 |  | 2.4 | 0 | 87.84 | -1313.3362 |  | 2.4 | 0 | 87.84 | -1313.3362 |  | 2.4 | 0 | 87.84 | -1313.3362
80 |  | 2 | 4.8 | 7.625 | 36.6 | 0.0465 | 44.8 | -176 | 30.5074 | -179.0317 |  | 0 | 60 | -2.79 | 41.6249 |  | 0 | 60 | -2.79 | 41.6249 |  | 0 | 60 | -2.79 | 41.6249 |  | 0 | 60 | -2.79 | 41.6249 |  | 0 | 60 | -2.79 | 41.6249 |  | 0 | 60 | -2.79 | 41.6249 |  | 0 | 60 | -2.79 | 41.6249 |  | 0 | 60 | -2.79 | 41.6249 |  | 0 | 59.8525 | -2.7831 | 41.5225 |  | 0 | 47.445 | -2.2062 | 32.9149 |  | 0 | 37.1644 | -1.7281 | 25.7828 |  | 0 | 28.5071 | -1.3256 | 19.7767 |  | 0 | 21.1166 | -0.98192 | 14.6496 |  | 0 | 14.7338 | -0.68512 | 10.2216 |  | 0 | 9.1659 | -0.42621 | 6.3588 |  | 0 | 4.2661 | -0.19837 | 2.9596 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 87.84 | -1310.5118 |  | 2.4 | 0 | 87.84 | -1310.5118 |  | 2.4 | 0 | 87.84 | -1310.5118 |  | 2.4 | 0 | 87.84 | -1310.5118 |  | 2.4 | 0 | 87.84 | -1310.5118 |  | 2.4 | 0 | 87.84 | -1310.5118 |  | 2.4 | 0 | 87.84 | -1310.5118 |  | 2.4 | 0 | 87.84 | -1310.5118
81 |  | 3 | 4.8 | 7.625 | 36.6 | 0.0465 | 40 | -176 | 25.7229 | -178.6458 |  | 0 | 60 | -2.79 | 41.5352 |  | 0 | 60 | -2.79 | 41.5352 |  | 0 | 60 | -2.79 | 41.5352 |  | 0 | 60 | -2.79 | 41.5352 |  | 0 | 60 | -2.79 | 41.5352 |  | 0 | 60 | -2.79 | 41.5352 |  | 0 | 60 | -2.79 | 41.5352 |  | 0 | 60 | -2.79 | 41.5352 |  | 0 | 59.7117 | -2.7766 | 41.3356 |  | 0 | 47.3174 | -2.2003 | 32.7556 |  | 0 | 37.0478 | -1.7227 | 25.6464 |  | 0 | 28.3996 | -1.3206 | 19.6597 |  | 0 | 21.017 | -0.97729 | 14.549 |  | 0 | 14.641 | -0.68081 | 10.1353 |  | 0 | 9.079 | -0.42217 | 6.285 |  | 0 | 4.1844 | -0.19457 | 2.8967 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 87.84 | -1307.6874 |  | 2.4 | 0 | 87.84 | -1307.6874 |  | 2.4 | 0 | 87.84 | -1307.6874 |  | 2.4 | 0 | 87.84 | -1307.6874 |  | 2.4 | 0 | 87.84 | -1307.6874 |  | 2.4 | 0 | 87.84 | -1307.6874 |  | 2.4 | 0 | 87.84 | -1307.6874 |  | 2.4 | 0 | 87.84 | -1307.6874
82 |  | 4 | 4.8 | 7.625 | 36.6 | 0.0465 | 35.2 | -176 | 20.9385 | -178.26 |  | 0 | 60 | -2.79 | 41.4454 |  | 0 | 60 | -2.79 | 41.4454 |  | 0 | 60 | -2.79 | 41.4454 |  | 0 | 60 | -2.79 | 41.4454 |  | 0 | 60 | -2.79 | 41.4454 |  | 0 | 60 | -2.79 | 41.4454 |  | 0 | 60 | -2.79 | 41.4454 |  | 0 | 60 | -2.79 | 41.4454 |  | 0 | 59.5709 | -2.77 | 41.149 |  | 0 | 47.1898 | -2.1943 | 32.5967 |  | 0 | 36.9311 | -1.7173 | 25.5104 |  | 0 | 28.2921 | -1.3156 | 19.543 |  | 0 | 20.9173 | -0.97266 | 14.4488 |  | 0 | 14.5482 | -0.67649 | 10.0493 |  | 0 | 8.9921 | -0.41813 | 6.2114 |  | 0 | 4.1027 | -0.19078 | 2.834 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 87.84 | -1304.8631 |  | 2.4 | 0 | 87.84 | -1304.8631 |  | 2.4 | 0 | 87.84 | -1304.8631 |  | 2.4 | 0 | 87.84 | -1304.8631 |  | 2.4 | 0 | 87.84 | -1304.8631 |  | 2.4 | 0 | 87.84 | -1304.8631 |  | 2.4 | 0 | 87.84 | -1304.8631 |  | 2.4 | 0 | 87.84 | -1304.8631
83 | b22 | 5 | 4.8 | 7.625 | 36.6 | 0.0465 | 30.4 | -176 | 16.154 | -177.8741 | b22 | 0 | 60 | -2.79 | 41.3557 | b22 | 0 | 60 | -2.79 | 41.3557 | b22 | 0 | 60 | -2.79 | 41.3557 | b22 | 0 | 60 | -2.79 | 41.3557 | b22 | 0 | 60 | -2.79 | 41.3557 | b22 | 0 | 60 | -2.79 | 41.3557 | b22 | 0 | 60 | -2.79 | 41.3557 | b22 | 0 | 60 | -2.79 | 41.3557 | b22 | 0 | 59.43 | -2.7635 | 40.9629 | b22 | 0 | 47.0622 | -2.1884 | 32.4382 | b22 | 0 | 36.8144 | -1.7119 | 25.3748 | b22 | 0 | 28.1846 | -1.3106 | 19.4266 | b22 | 0 | 20.8177 | -0.96802 | 14.3489 | b22 | 0 | 14.4554 | -0.67217 | 9.9635 | b22 | 0 | 8.9052 | -0.41409 | 6.138 | b22 | 0 | 4.021 | -0.18698 | 2.7715 | b22 | 0 | 0 | 0 | 0 | b22 | 2.4 | 0 | 87.84 | -1302.0387 | b22 | 2.4 | 0 | 87.84 | -1302.0387 | b22 | 2.4 | 0 | 87.84 | -1302.0387 | b22 | 2.4 | 0 | 87.84 | -1302.0387 | b22 | 2.4 | 0 | 87.84 | -1302.0387 | b22 | 2.4 | 0 | 87.84 | -1302.0387 | b22 | 2.4 | 0 | 87.84 | -1302.0387 | b22 | 2.4 | 0 | 87.84 | -1302.0387
84 |  | 6 | 4.8 | 7.625 | 36.6 | 0.0465 | 25.6 | -176 | 11.3695 | -177.4883 |  | 0 | 60 | -2.79 | 41.266 |  | 0 | 60 | -2.79 | 41.266 |  | 0 | 60 | -2.79 | 41.266 |  | 0 | 60 | -2.79 | 41.266 |  | 0 | 60 | -2.79 | 41.266 |  | 0 | 60 | -2.79 | 41.266 |  | 0 | 60 | -2.79 | 41.266 |  | 0 | 60 | -2.79 | 41.266 |  | 0 | 59.2892 | -2.7569 | 40.7772 |  | 0 | 46.9345 | -2.1825 | 32.28 |  | 0 | 36.6977 | -1.7064 | 25.2395 |  | 0 | 28.0772 | -1.3056 | 19.3106 |  | 0 | 20.7181 | -0.96339 | 14.2492 |  | 0 | 14.3626 | -0.66786 | 9.8781 |  | 0 | 8.8183 | -0.41005 | 6.0649 |  | 0 | 3.9394 | -0.18318 | 2.7094 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 87.84 | -1299.2143 |  | 2.4 | 0 | 87.84 | -1299.2143 |  | 2.4 | 0 | 87.84 | -1299.2143 |  | 2.4 | 0 | 87.84 | -1299.2143 |  | 2.4 | 0 | 87.84 | -1299.2143 |  | 2.4 | 0 | 87.84 | -1299.2143 |  | 2.4 | 0 | 87.84 | -1299.2143 |  | 2.4 | 0 | 87.84 | -1299.2143
85 |  | 7 | 4.8 | 7.625 | 36.6 | 0.0465 | 20.8 | -176 | 6.5851 | -177.1024 |  | 0 | 60 | -2.79 | 41.1763 |  | 0 | 60 | -2.79 | 41.1763 |  | 0 | 60 | -2.79 | 41.1763 |  | 0 | 60 | -2.79 | 41.1763 |  | 0 | 60 | -2.79 | 41.1763 |  | 0 | 60 | -2.79 | 41.1763 |  | 0 | 60 | -2.79 | 41.1763 |  | 0 | 60 | -2.79 | 41.1763 |  | 0 | 59.1484 | -2.7504 | 40.5919 |  | 0 | 46.8069 | -2.1765 | 32.1223 |  | 0 | 36.581 | -1.701 | 25.1045 |  | 0 | 27.9697 | -1.3006 | 19.1948 |  | 0 | 20.6185 | -0.95876 | 14.1499 |  | 0 | 14.2697 | -0.66354 | 9.7929 |  | 0 | 8.7314 | -0.40601 | 5.9921 |  | 0 | 3.8577 | -0.17938 | 2.6474 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 87.84 | -1296.3899 |  | 2.4 | 0 | 87.84 | -1296.3899 |  | 2.4 | 0 | 87.84 | -1296.3899 |  | 2.4 | 0 | 87.84 | -1296.3899 |  | 2.4 | 0 | 87.84 | -1296.3899 |  | 2.4 | 0 | 87.84 | -1296.3899 |  | 2.4 | 0 | 87.84 | -1296.3899 |  | 2.4 | 0 | 87.84 | -1296.3899
86 |  | 8 | 4.8 | 7.625 | 36.6 | 0.0465 | 16 | -176 | 1.8006 | -176.7166 |  | 0 | 60 | -2.79 | 41.0866 |  | 0 | 60 | -2.79 | 41.0866 |  | 0 | 60 | -2.79 | 41.0866 |  | 0 | 60 | -2.79 | 41.0866 |  | 0 | 60 | -2.79 | 41.0866 |  | 0 | 60 | -2.79 | 41.0866 |  | 0 | 60 | -2.79 | 41.0866 |  | 0 | 60 | -2.79 | 41.0866 |  | 0 | 59.0076 | -2.7439 | 40.407 |  | 0 | 46.6793 | -2.1706 | 31.9649 |  | 0 | 36.4643 | -1.6956 | 24.9699 |  | 0 | 27.8622 | -1.2956 | 19.0794 |  | 0 | 20.5189 | -0.95413 | 14.0509 |  | 0 | 14.1769 | -0.65923 | 9.708 |  | 0 | 8.6445 | -0.40197 | 5.9196 |  | 0 | 3.776 | -0.17558 | 2.5857 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 87.84 | -1293.5655 |  | 2.4 | 0 | 87.84 | -1293.5655 |  | 2.4 | 0 | 87.84 | -1293.5655 |  | 2.4 | 0 | 87.84 | -1293.5655 |  | 2.4 | 0 | 87.84 | -1293.5655 |  | 2.4 | 0 | 87.84 | -1293.5655 |  | 2.4 | 0 | 87.84 | -1293.5655 |  | 2.4 | 0 | 87.84 | -1293.5655
87 |  | 9 | 4.8 | 7.625 | 36.6 | 0.0465 | 11.2 | -176 | -2.9839 | -176.3308 |  | 0 | 60 | -2.79 | 40.9969 |  | 0 | 60 | -2.79 | 40.9969 |  | 0 | 60 | -2.79 | 40.9969 |  | 0 | 60 | -2.79 | 40.9969 |  | 0 | 60 | -2.79 | 40.9969 |  | 0 | 60 | -2.79 | 40.9969 |  | 0 | 60 | -2.79 | 40.9969 |  | 0 | 60 | -2.79 | 40.9969 |  | 0 | 58.8667 | -2.7373 | 40.2226 |  | 0 | 46.5517 | -2.1647 | 31.8079 |  | 0 | 36.3477 | -1.6902 | 24.8357 |  | 0 | 27.7547 | -1.2906 | 18.9643 |  | 0 | 20.4193 | -0.9495 | 13.9521 |  | 0 | 14.0841 | -0.65491 | 9.6234 |  | 0 | 8.5576 | -0.39793 | 5.8473 |  | 0 | 3.6943 | -0.17179 | 2.5243 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 87.84 | -1290.7412 |  | 2.4 | 0 | 87.84 | -1290.7412 |  | 2.4 | 0 | 87.84 | -1290.7412 |  | 2.4 | 0 | 87.84 | -1290.7412 |  | 2.4 | 0 | 87.84 | -1290.7412 |  | 2.4 | 0 | 87.84 | -1290.7412 |  | 2.4 | 0 | 87.84 | -1290.7412 |  | 2.4 | 0 | 87.84 | -1290.7412
88 |  | 10 | 4.8 | 7.625 | 36.6 | 0.0465 | 6.4 | -176 | -7.7683 | -175.9449 |  | 0 | 60 | -2.79 | 40.9072 |  | 0 | 60 | -2.79 | 40.9072 |  | 0 | 60 | -2.79 | 40.9072 |  | 0 | 60 | -2.79 | 40.9072 |  | 0 | 60 | -2.79 | 40.9072 |  | 0 | 60 | -2.79 | 40.9072 |  | 0 | 60 | -2.79 | 40.9072 |  | 0 | 60 | -2.79 | 40.9072 |  | 0 | 58.7259 | -2.7308 | 40.0385 |  | 0 | 46.424 | -2.1587 | 31.6513 |  | 0 | 36.231 | -1.6847 | 24.7018 |  | 0 | 27.6473 | -1.2856 | 18.8495 |  | 0 | 20.3197 | -0.94487 | 13.8537 |  | 0 | 13.9913 | -0.65059 | 9.5391 |  | 0 | 8.4707 | -0.39389 | 5.7752 |  | 0 | 3.6126 | -0.16799 | 2.463 |  | 0 | 0 | 0 | 0 |  | 2.4 | 0 | 87.84 | -1287.9168 |  | 2.4 | 0 | 87.84 | -1287.9168 |  | 2.4 | 0 | 87.84 | -1287.9168 |  | 2.4 | 0 | 87.84 | -1287.9168 |  | 2.4 | 0 | 87.84 | -1287.9168 |  | 2.4 | 0 | 87.84 | -1287.9168 |  | 2.4 | 0 | 87.84 | -1287.9168 |  | 2.4 | 0 | 87.84 | -1287.9168
|  |  | Am: 4234.5; As: 9.9433 |  |  |  | -596.6 | -261.4263 |  |  |  | 1863.4369 | 35389.7948 |  |  |  | 2202.0069 | 39688.0596 |  |  |  | 2690.9589 | 45048.7103 |  |  |  | 3029.7833 | 48095.0068 |  |  |  | 3518.6844 | 51689.3561 |  |  |  | 3857.5596 | 53480.5608 |  |  |  | 4346.439 | 55309.0549 |  |  |  | 4688.3255 | 55802.0951 |  |  |  | 5034.7896 | 55689.2915 |  |  |  | 5370.9221 | 55264.1677 |  |  |  | 5699.2462 | 54507.2417 |  |  |  | 6021.3961 | 53405.5089 |  |  |  | 6338.7173 | 51948.4459 |  |  |  | 6652.0494 | 50129.587 |  |  |  | 6962.1975 | 47942.3287 |  |  |  | 7267.98 | 45406.8698 |  |  |  | 10162.8 | 6672.4505 |  |  |  | 10162.8 | 6672.4505 |  |  |  | 10162.8 | 6672.4505 |  |  |  | 10162.8 | 6672.4505 |  |  |  | 10162.8 | 6672.4505 |  |  |  | 10162.8 | 6672.4505 |  |  |  | 10162.8 | 6672.4505 |  |  |  | 10162.8 | 6672.4505