## FOOTING
[5 empty] | PROJECT : | [9 empty] | PAGE :
[5 empty] | CLIENT : | [9 empty] | DESIGN BY :
[5 empty] | JOB NO. : |  |  |  | DATE : | [5 empty] | REVIEW BY :
Rectangular Machine or Tank Footing Design Based on ACI 318-19
INPUT DATA | [8 empty] | DESIGN SUMMARY
MACHINE WIDTH |  |  |  | c1 | = | 40 | ft |  | FOOTING WIDTH |  |  |  | B | = | 24 | ft
MACHINE DEPTH |  |  |  | c2 | = | 20 | ft |  | FOOTING LENGTH |  |  |  | L | = | 44 | ft
BASE PLATE WIDTH |  |  |  | b1 | = | 42 | ft |  | FOOTING THICKNESS |  |  |  | T | = | 18 | in
BASE PLATE DEPTH |  |  |  | b2 | = | 22 | ft |  | LONGITUDINAL REINF., TOP |  |  |  |  | 1 # 8
FOOTING CONCRETE STRENGTH |  |  |  | fc' | = | 2.5 | ksi |  | LONGITUDINAL REINF., BOT. |  |  |  |  | 17 # 8 @ 17 in o.c.
REBAR YIELD STRESS |  |  |  | fy | = | 60 | ksi |  | TRANSVERSE REINF., BOT. |  |  |  |  | 30 # 8 @ 18 in o.c.
AXIAL DEAD LOAD |  |  |  | PDL | = | 23 | k
AXIAL LIVE LOAD |  |  |  | PLL | = | 1450 | k
LATERAL LOAD (0=WIND, 1=SEISMIC) |  |  |  |  | = | 0 | Wind,SD | [10 empty] | <== Tips: | Please check both perpendicular directions, because bigger wind loads from wider side.
WIND AXIAL LOAD |  |  |  | PLAT | = | 4.6 | k, SD
WIND MOMENT LOAD |  |  |  | MLAT | = | 11.5 | ft-k, SD
WIND SHEAR LOAD |  |  |  | VLAT | = | 4.6 | k, SD
SURCHARGE |  |  |  | qs | = | 0.1 | ksf
SOIL WEIGHT |  |  |  | ws | = | 0.11 | kcf
FOOTING EMBEDMENT DEPTH |  |  |  | Df | = | 2.5 | ft
FOOTING THICKNESS |  |  |  | T | = | 18 | in
ALLOW SOIL PRESSURE |  |  |  | Qa | = | 2 | ksf
FOOTING WIDTH |  |  |  | B | = | 24 | ft
FOOTING LENGTH |  |  |  | L | = | 44 | ft
REINFORCING SIZE |  |  |  |  | # | 8
THE FOOTING DESIGN IS ADEQUATE.
ANALYSIS
DESIGN LOADS AT TOP OF FOOTING (IBC 1605.2 & ACI 318 5.3)
CASE 1: |  | DL + LL |  | P | = | 1473 | kips |  |  | 1.2 DL + 1.6 LL |  |  | Pu | = | 2347.6 | kips
|  |  |  | M | = | 0 | ft-kips | [5 empty] | Mu | = | 0 | ft-kips
|  |  |  | e | = | 0 | ft, fr cl ftg | [5 empty] | eu | = | 0 | ft, fr cl ftg
CASE 2: |  | DL + LL + 0.6(1.3) W |  | P | = | 1476.588 | kips |  |  | 1.2 DL + LL + 1.0 W |  |  | Pu | = | 1482.2 | kips
|  |  |  | M | = | 12.558 | ft-kips | [5 empty] | Mu | = | 11.5 | ft-kips
|  |  |  | V | = | 3.588 | kips | [5 empty] | Vu | = | 4.6 | kips
|  |  |  | e | = | 0.0085047 | ft, fr cl ftg | [5 empty] | eu | = | 0.0077587 | ft, fr cl ftg
CASE 3: |  | DL + LL + 0.6(0.65) W |  | P | = | 1474.794 | kips |  |  | 0.9 DL+ 1.0 W |  |  | Pu | = | 25.3 | kips
|  |  |  | M | = | 8.05 | ft-kips | [5 empty] | Mu | = | 11.5 | ft-kips
|  |  |  | V | = | 2.3 | kips | [5 empty] | Vu | = | 4.6 | kips
|  |  |  | e | = | 0.0054584 | ft, fr cl ftg | [5 empty] | eu | = | 0.45455 | ft, fr cl ftg
CHECK OVERTURNING FACTOR (2021 IBC 1605.2.1, 1808.3.1, & ASCE 7-22 12.13.4)
| MR / MO = |  | 828871999999.9999 | > | F = 1.0 / 0.9 = |  | 1.1111 |  | [Satisfactory]
| Where | MO = | MLAT + VLAT T - PLATL2 = |  |  |  | 1e-08 | k-ft
|  | Pftg = | (0.15 kcf) T B L = |  |  | 237.6 | k, footing weight
|  | Psoil = | ws (Df - T) B L = |  |  | 116.16 | k, soil weight
|  | MR = | PDLL2 + 0.5 (Pftg + Psoil) L = |  |  |  | 8288.72 | k-ft
FOR REVERSED LATERAL LOADS,
| MR / MO = |  | 828871999999.9999 | > | F = 1.0 / 0.9 |  |  |  | [Satisfactory]
| Where | MO = | MLAT + VLAT Df - PLATL1 = |  |  |  | 1e-08 | k-ft
|  | MR = | PDLL1 + 0.5 (Pftg + Psoil) L = |  |  |  | 8288.72 | k-ft
CHECK SLIDING (2021 IBC 1807.2.3)
1.5 | (VLat, ASD) = |  |  | 4.14 | kips | < | m SW = |  | 104.24 | kips |  | [Satisfactory]
| Where | ` | m = | 0.4
(cont'd)
CHECK SOIL BEARING CAPACITY (ACI 318 13.3.1.1)
| Service Loads |  |  | CASE 1 |  |  | CASE 2 |  |  | CASE 3
| P |  |  | 1473 |  |  | 1476.588 |  |  | 1474.794 |  |  | k
| e |  |  | 0 |  |  | 0.01215 |  |  | 0.0077977 |  | ft (from center of footing)
| qs B L |  |  | 105.6 |  |  | 105.6 |  |  | 63.36 |  | k, (surcharge load)
| (0.15-ws)T B L |  |  | 63.36 |  |  | 63.36 |  |  | 38.016 |  | k, (footing increased)
| S P |  |  | 1641.96 |  |  | 1645.548 |  |  | 1576.17 |  |  | k
| eL |  |  | 0 | < L/6 |  | 0.010902 | < L/6 |  | 0.0072962 | < L/6 |  | ft
| eB |  |  | 0 | < B/6 |  | 0 | < B/6 |  | 0 | < B/6 |  | ft
| qL |  |  | 37.3173 |  |  | 37.4544 |  |  | 35.8577 |  |  | k / ft
| qmax |  |  | 1.5549 |  |  | 1.5606 |  |  | 1.4941 |  |  | ksf
| qallow |  |  | 2 |  |  | 2.6667 |  |  | 2.6667 |  |  | ksf
Where
[Satisfactory]
DESIGN FLEXURE & CHECK FLEXURE SHEAR
(ACI 318 13, 21, & 22)
FACTORED SOIL PRESSURE
| Factored Loads |  |  | CASE 1 |  |  | CASE 2 |  |  | CASE 3
| Pu |  |  | 2347.6 |  |  | 1482.2 |  |  | 25.3 |  |  | k
| eu |  |  | 0 |  |  | 0.012414 |  |  | 0.72727 |  |  | ft
| g qs B L |  |  | 168.96 |  |  | 105.6 |  |  | 0 |  | k, (factored surcharge load)
| g[0.15T + ws(Df - T)]BL |  |  | 424.512 |  |  | 424.512 |  |  | 318.384 |  | k, (factored footing & backfill loads)
| S Pu |  |  | 2941.072 |  |  | 2012.312 |  |  | 343.684 |  |  | k
| eu |  |  | 0 | < L/6 |  | 0.0091437 | < L/6 |  | 0.053538 | < L/6 |  | ft
| qu, max |  |  | 2.7851 |  |  | 1.908 |  |  | 0.32783 |  |  | ksf
FOOTING MOMENT & SHEAR AT LONGITUDINAL SECTIONS FOR CASE 1
| Section |  |  |  | 0 | 0.125 L | 0.25 L | 0.375 L | CenL | CenR | 0.625 L | 0.75 L | 0.875 L | L
| Xu (ft, dist. from left of footing) |  |  |  | 0 | 5.5 | 11 | 16.5 | 22 | 22 | 27.5 | 33 | 38.5 | 44
| Mu,machine (ft-k) |  |  |  | 0 | -806.9875 | -3227.95 | -7262.8875 | -12911.8 | -12911.8 | -20174.6875 | -29051.55 | -39542.3875 | -51647.2
| Vu,machine (k) |  |  |  | 0 | 293.45 | 586.9 | 880.35 | 1173.8 | 1173.8 | 1467.25 | 1760.7 | 2054.15 | 2347.6
| Pu,surch (klf) |  |  |  | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84 | 3.84
| Mu,surch (ft-k) |  |  |  | 0 | -58.08 | -232.32 | -522.72 | -929.28 | -929.28 | -1452 | -2090.88 | -2845.92 | -3717.12
| Vu,surch (k) |  |  |  | 0 | 21.12 | 42.24 | 63.36 | 84.48 | 84.48 | 105.6 | 126.72 | 147.84 | 168.96
| Pu,ftg & fill (klf) |  |  |  | 9.648 | 9.648 | 9.648 | 9.648 | 9.648 | 9.648 | 9.648 | 9.648 | 9.648 | 9.648
| Mu,ftg & fill (ft-k) |  |  |  | 0 | -145.926 | -583.704 | -1313.334 | -2334.816 | -2334.816 | -3648.15 | -5253.336 | -7150.374 | -9339.264
| Vu,ftg & fill (k) |  |  |  | 0 | 53.064 | 106.128 | 159.192 | 212.256 | 212.256 | 265.32 | 318.384 | 371.448 | 424.512
| qu,soil (ksf) |  |  |  | 2.7851 | 2.7851 | 2.7851 | 2.7851 | 2.7851 | 2.7851 | 2.7851 | 2.7851 | 2.7851 | 2.7851
| Mu,soil (ft-k) |  |  |  | 0 | 1010.9935 | 4043.974 | 9098.9415 | 16175.896 | 16175.896 | 25274.8375 | 36395.766 | 49538.6815 | 64703.584
| Vu,soil (k) |  |  |  | 0 | -367.634 | -735.268 | -1102.902 | -1470.536 | -1470.536 | -1838.17 | -2205.804 | -2573.438 | -2941.072
| S Mu (ft-k) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S Vu (kips) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(cont'd)
FOOTING MOMENT & SHEAR AT LONGITUDINAL SECTIONS FOR CASE 2
| Section |  |  |  | 0 | 0.125 L | 0.25 L | 0.375 L | CenL | CenR | 0.625 L | 0.75 L | 0.875 L | L
| Xu (ft, dist. from left of footing) |  |  |  | 0 | 5.5 | 11 | 16.5 | 22 | 22 | 27.5 | 33 | 38.5 | 44
| Mu,machine (ft-k) |  |  |  | 0 | -509.2187 | -2036.875 | -4582.9687 | -8147.5 | -8147.5 | -12730.4687 | -18331.875 | -24951.7187 | -32590
| Vu,machine (k) |  |  |  | 0 | 185.275 | 370.55 | 555.825 | 741.1 | 741.1 | 926.375 | 1111.65 | 1296.925 | 1482.2
| Pu,surch (klf) |  |  |  | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
| Mu,surch (ft-k) |  |  |  | 0 | -36.3 | -145.2 | -326.7 | -580.8 | -580.8 | -907.5 | -1306.8 | -1778.7 | -2323.2
| Vu,surch (k) |  |  |  | 0 | 13.2 | 26.4 | 39.6 | 52.8 | 52.8 | 66 | 79.2 | 92.4 | 105.6
| Pu,ftg & fill (klf) |  |  |  | 9.648 | 9.648 | 9.648 | 9.648 | 9.648 | 9.648 | 9.648 | 9.648 | 9.648 | 9.648
| Mu,ftg & fill (ft-k) |  |  |  | 0 | -145.926 | -583.704 | -1313.334 | -2334.816 | -2334.816 | -3648.15 | -5253.336 | -7150.374 | -9339.264
| Vu,ftg & fill (k) |  |  |  | 0 | 53.064 | 106.128 | 159.192 | 212.256 | 212.256 | 265.32 | 318.384 | 371.448 | 424.512
| qu,soil (ksf) |  |  |  | 1.9032 | 1.9038 | 1.9044 | 1.905 | 1.9056 | 1.9056 | 1.9062 | 1.9068 | 1.9074 | 1.908
| Mu,soil (ft-k) |  |  |  | 0 | 690.9416 | 2764.054 | 6219.7684 | 11058.516 | 11058.516 | 17280.7281 | 24886.836 | 33877.2709 | 44252.464
| Vu,soil (k) |  |  |  | 0 | -251.2646 | -502.6075 | -754.0289 | -1005.5287 | -1005.5287 | -1257.1069 | -1508.7635 | -1760.4986 | -2012.312
| S Mu (ft-k) |  |  |  | 0 | -0.50312 | -1.725 | -3.2344 | -4.6 | -4.6 | -5.3906 | -5.175 | -3.5219 | 0
| S Vu (kips) |  |  |  | 0 | 0.27443 | 0.47045 | 0.58807 | 0.62727 | 0.62727 | 0.58807 | 0.47045 | 0.27443 | 0
FOOTING MOMENT & SHEAR AT LONGITUDINAL SECTIONS FOR CASE 3
| Section |  |  |  | 0 | 0.125 L | 0.25 L | 0.375 L | CenL | CenR | 0.625 L | 0.75 L | 0.875 L | L
| Xu (ft, dist. from left of footing) |  |  |  | 0 | 5.5 | 11 | 16.5 | 22 | 22 | 27.5 | 33 | 38.5 | 44
| Mu,machine (ft-k) |  |  |  | 0 | -8.4094 | -33.6375 | -75.6844 | -134.55 | -134.55 | -210.2344 | -302.7375 | -412.0594 | -538.2
| Vu,machine (k) |  |  |  | 0 | 3.1625 | 6.325 | 9.4875 | 12.65 | 12.65 | 15.8125 | 18.975 | 22.1375 | 25.3
| Pu,surch (klf) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Mu,surch (ft-k) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vu,surch (k) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pu,ftg & fill (klf) |  |  |  | 7.236 | 7.236 | 7.236 | 7.236 | 7.236 | 7.236 | 7.236 | 7.236 | 7.236 | 7.236
| Mu,ftg & fill (ft-k) |  |  |  | 0 | -109.4445 | -437.778 | -985.0005 | -1751.112 | -1751.112 | -2736.1125 | -3940.002 | -5362.7805 | -7004.448
| Vu,ftg & fill (k) |  |  |  | 0 | 39.798 | 79.596 | 119.394 | 159.192 | 159.192 | 198.99 | 238.788 | 278.586 | 318.384
| qu,soil (ksf) |  |  |  | 0.32308 | 0.32368 | 0.32427 | 0.32486 | 0.32546 | 0.32546 | 0.32605 | 0.32665 | 0.32724 | 0.32783
| Mu,soil (ft-k) |  |  |  | 0 | 117.3508 | 469.6905 | 1057.4505 | 1881.062 | 1881.062 | 2940.9563 | 4237.5645 | 5771.318 | 7542.648
| Vu,soil (k) |  |  |  | 0 | -42.6861 | -85.4505 | -128.2934 | -171.2147 | -171.2147 | -214.2144 | -257.2925 | -300.4491 | -343.684
| S Mu (ft-k) |  |  |  | 0 | -0.50312 | -1.725 | -3.2344 | -4.6 | -4.6 | -5.3906 | -5.175 | -3.5219 | 0
| S Vu (kips) |  |  |  | 0 | 0.27443 | 0.47045 | 0.58807 | 0.62727 | 0.62727 | 0.58807 | 0.47045 | 0.27443 | 0
DESIGN FLEXURE
| Location |  |  | Mu,max |  | d (in) | rmin | rreqD | rmax | smax |  | use |  | rprovD
| Top Longitudinal |  |  | 5.3906 | ft-k | 15.5 | 2.3059e-05 | 1.7295e-05 | 0.012902 | no limit |  | 1 # 8 |  | 0.00017697
| Bottom Longitudinal |  |  | 33.4213 | ft-k | 14.5 | 0.00016361 | 0.00012271 | 0.012902 | 18 |  | 17 # 8 @ 17 in o.c. |  | 0.003216
| Bottom Transverse |  |  | 1.3926 | ft-k / ft | 14 | 0.00017553 | 0.00013164 | 0.012902 | 18 |  | 30 # 8 @ 18 in o.c. |  | 0.0032062
[Satisfactory]
CHECK FLEXURE SHEAR
| Direction |  |  | Vu,max |  | fVc = 2 f b d (fc')0.5 |  |  |  | check Vu < f Vc
| Longitudinal |  |  | 0 | k |  | 313.2 | k |  | [Satisfactory]
| Transverse |  |  | 0 | k / ft |  | 12.6 | k / ft |  | [Satisfactory]
CHECK PUNCHING SHEAR (ACI 318 13.2.7.2, 22.6.4.1, 22.6.4.3, & 8.4.2.3)
| Case | Pu | Mu | b1 | b2 | b0 | gv | bc | y | Af | Ap | R | J | vu (psi) | f vc
| 1 | 2347.6 | 0 | 506 | 266 | 10.7222 | 0.47903 | 1.9023 | 2 | 1056 | 150.1111 | 2077.9249 | 37580.2283 | 12.4757 | 150
| 2 | 1482.2 | 11.5 | 506 | 266 | 10.7222 | 0.47903 | 1.9023 | 2 | 1056 | 150.1111 | 1311.9357 | 37580.2283 | 7.8769 | 150
| 3 | 25.3 | 11.5 | 506 | 266 | 10.7222 | 0.47903 | 1.9023 | 2 | 1056 | 150.1111 | 22.3937 | 37580.2283 | 0.1346 | 150
[Satisfactory]
| where | f | = | 0.75 | , (ACI 318 21.2)
LICENSE NUMBER: M 492263176 - XXXXXX XXXXXX, S.E. - ASCE 7-22 Package License
www.Engineering-International.com
|  |  | c1 | = | 480 | in
|  |  | c2 | = | 240 | in
|  |  | b1 | = | 504 | in
|  |  | b2 | = | 264 | in
|  |  | B1 | = | 12 | ft
|  |  | B2 | = | 12 | ft
|  |  | L1 | = | 22 | ft
|  |  | L2 | = | 22 | ft
|  |  | SIZE | DIAM. | AREA
|  |  | # | in | in2
|  |  | 3 | 0.375 | 0.11
|  |  | 4 | 0.5 | 0.2
|  |  | 5 | 0.625 | 0.31
|  |  | 6 | 0.75 | 0.44
|  |  | 7 | 0.875 | 0.6
|  |  | 8 | 1 | 0.79
|  |  | 9 | 1.128 | 1
|  |  | 10 | 1.27 | 1.27
|  |  | 11 | 1.41 | 1.56
|  |  | 14 | 1.693 | 2.25
|  |  | 18 | 2.257 | 4
|  | LONGITUDINAL REINF., TOP |  |  |  | 1 | # | 8
|  | LONGITUDINAL REINF., BOT. |  |  |  | 17 | # | 8 | @ | 17 | in o.c.
|  | TRANSVERSE REINF., BOT. |  |  |  | 30 | # | 8 | @ | 18 | in o.c.
160